|  |  |  | Building Life Safety Systems Testing |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| Insert Logo Here | Service Company Information (Address, Telephone, & Contact Information |  |  |  |  |  |  |
|  |  |  | Date of Service: | Last Service Date: |  | Work Order Number: |  |
| Building Name: |  |  | Contact Person: |  | Phone: |  |  |
|  |  |  |  |  | Fax: |  |  |
| Address: |  |  | Owner/Strata Number: |  | Phone: |  |  |
|  |  |  |  |  | Fax: |  |  |
| City: |  | Postal Code: | Monitoring/Central Station: |  | Phone: |  |  |
|  |  |  |  |  | Fax: |  |  |

| This form is intended to provide the owner or fire inspector with an overview of what fire protection systems exist in the building and which systems |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| were inspected and tested by a qualified technician. The applicable reports indicated below are attached hereto and comprise |  |  |  |  | pages. |
| The attached reports comply with Canadian Inspection Standards upon which they are based. |  |  |  |  |  |
| There is fire protection equipment located at the above referenced address that has not been tested in accordance with the Provincial Fire Code. YES NO |  |  |  |  |  |
|  | Estimated Time To Test Building: |  |  | Man Hours |  |
|  | Actual Time to Test Building: |  |  | Man Hours |  |

| Building Life Safety & Emergency Systems |  | ## Tested By FP # | Initial | Comments |
| --- | --- | --- | --- | --- |
| Fire Alarm System Test Report |  |  |  |  |
| Smoke Control System Test Report |  |  |  |  |
| Unit Emergency Lighting Test Report |  |  |  |  |
| Sprinkler Systems Test Report |  |  |  |  |
| Standpipe Systems Test Report |  |  |  |  |
| Fire Pump Test Report |  |  |  |  |
| Backflow Prevention Device Test Report |  |  |  |  |
| Emergency Generator Set Test Report |  |  |  |  |
| Fixed Extinguishment System Test Report |  |  |  |  |
| Fire Extinguishers Test Report |  |  |  |  |

| The information on this form (and in the documents attached here-to) attest to the fact that the equipment listed here-in was tested/inspected in conformance with applicable codes, bylaws, standards, and the manufacturer’s requirements by a qualified technician. The equipment was left in an operational condition except as noted in the spaces marked “comments”. This document has been provided to the building owner’s representative who has acknowledged receipt of same below. A copy should be maintained on the premises for examination by the Fire Marshal or Inspector at their request. |  |  |  |
| --- | --- | --- | --- |
| Company Name |  |  |  |
| Service Manager |  | Date | Owner or Authorized Agent |

|  |  |  | Building Fire Alarm/EVAC System Testing |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Insert Logo Here | Service Company Information (Address, Telephone, & Contact Information |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  | Date of Service: |  | Last Service Date: |  |  |  | Work Order Number: |  |  |  |
|  |  |  | Annual Inspection | Special Inspection/Audit |  |  |  |  |  |  | Direct Connection yes no |  |
|  |  |  | Single Stage | Two Stage |  |  | Number of Conventional Zones: |  |  |  |  |  |
|  |  |  |  |  |  |  | Initiating: |  |  |  |  |  |
|  |  |  | Addressable | Conventional |  |  | Notification: |  |  |  |  |  |
|  |  |  |  |  |  |  | Voice Paging: |  |  |  |  |  |
|  |  |  | Manufacturer: |  |  | Model Number: |  |  |  | ULC Serial Number: |  |  |
| Building Name: |  |  | Contact Person: |  |  |  |  | Phone: |  |  |  |  |
|  |  |  |  |  |  |  |  | Fax: |  |  |  |  |
| Address: |  |  | Owner/Property Manager/Strata Number: |  |  |  |  | Phone: |  |  |  |  |
|  |  |  |  |  |  |  |  | Fax: |  |  |  |  |
| City: |  | Postal Code: | Monitoring/Central Station: |  |  |  |  | Phone: |  |  |  |  |
|  |  |  |  |  |  |  |  | Fax: |  |  |  |  |

| Yes |  |  | No |  | Summary | (FOLLOWS CAN/ULC-S536-13 Appendix “C”, FIRE ALARM SYSTEM ANNUAL TEST & INSPECTION REPORT) |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  |  |  | The fire alarm system is now fully functional without deficiencies. |  |  |  |  |  |  |
|  |  |  |  |  | The fire alarm system has: deficiencies remarks noted on the pages attached. |  |  |  |  |  |  |
|  |  |  |  |  | The entire fire alarm system has been tested in accordance with ULC/CAN-S536. |  |  |  |  |  |  |
|  |  |  |  |  | The fire alarm system has been tested in accordance with ULC/CAN-S537. |  |  |  |  |  |  |
|  |  |  |  |  | The system is tagged/labeled as having been tested in accordance with ULC CAN4-S537. |  |  |  |  |  |  |
|  |  |  |  |  | The fire alarm system documentation is on site and includes a description of the system. |  |  |  |  |  |  |
|  |  |  |  |  | Sequence of operation confirmed and tested. |  |  |  |  |  |  |
|  |  |  |  |  | A copy of this report will be given to: |  |  |  | (the owner or owner’s representative for the building). |  |  |
| Yes | NA |  |  | Technician’s Post Test Checklist |  |  |  |  |  |  |  |
|  |  |  |  |  | Reconnect time limit cutouts? |  |  |  |  |  |  |
|  |  |  |  |  | Reconnect ancillary functions? |  |  |  |  |  |  |
|  |  |  |  |  | Reconnect ancillary functions (off site connections)? |  |  | Estimated number of End-of-Line Resistors*: |  |  |  |
|  |  |  |  |  | Reconnect signal power? |  |  | Actual number of End-of-Line Resistors tested: |  |  |  |
|  |  |  |  |  | Advise fire department that testing is completed? |  |  | * (Determined by the total number of conventional zones noted above.) |  |  |  |
|  |  |  |  |  | Advise central monitoring facility that testing is completed? |  |  |  |  |  |  |
|  |  |  |  |  | Ensure that the fire alarm system is fully functional? |  |  |  |  |  |  |

| Certification |  |  |  |  |
| --- | --- | --- | --- | --- |
| The information on this form (and in the documents attached here-to) attest to the fact that the equipment listed here-in was tested/inspected in conformance with applicable codes, bylaws, standards, and the manufacturer’s requirements by a qualified technician. The equipment was left in an operational condition except as noted in the spaces marked “Remarks”. This document has been provided to the building owner (or their authorized representative) who has acknowledged receipt of same below. A copy should be maintained on the premises for examination by the Fire Marshal or Inspector at their request. |  |  |  |  |
| Company: |  |  |  |  |
| Supervising/Primary Technician Name |  | Certification Number/Stamp | Date | Signature |
| Company: |  |  |  |  |
| Technician Conducting Test and Inspection |  | Certification Number/Stamp | Date | Signature |

| Date: |  | Annual Special Inspection/Audit |  |
| --- | --- | --- | --- |
| Building Name: |  | Address: |  |

| Documentation |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  |  |  |  | Yes | No | N/A |
| Instructions for resetting the system and silencing alarm signals. |  |  |  |  |  |  |  |  |
| Instructions for silencing the trouble signal and action to be taken when the trouble signal sounds. |  |  |  |  |  |  |  |  |
| Description of the function of each operating control and indicator on the fire alarm control unit. |  |  |  |  |  |  |  |  |
| Description of the area or fire zone protected by each alarm detection circuit (this may be in the form of a list or plan drawing). |  |  |  |  |  |  |  |  |
| Description of alarm signal operation. |  |  |  |  |  |  |  |  |
| Description of ancillary equipment controlled by the fire alarm system. |  |  |  |  |  |  |  |  |
| Description of elevator homing functions activated by the fire alarm system. |  |  |  |  |  |  |  |  |
| Magnetic door holder release activated by fire alarm system? |  |  |  |  |  |  |  |  |
| Fire shutter release activated by fire alarm system? |  |  |  |  |  |  |  |  |
| Extinguishing system controlled by fire alarm system? |  |  |  |  |  |  |  |  |
| Fire Safety Plan documentation on site? |  |  |  |  |  |  |  |  |
| Instructions to Occupants/Evacuation Floor Plans are posted. |  |  |  |  |  |  |  |  |
| In systems that provide logical control of a smoke control system, documentation is on site and includes a sequence of operation of the smoke control system. |  |  |  |  |  |  |  |  |
| Smoke control installed in accordance with Measure: |  |  |  |  |  |  |  |  |
| Building diagrams are on site that clearly indicate the type and location of all smoke control equipment (fans, dampers, etc.). |  |  |  |  |  |  |  |  |
| Additional documentation relating to smoke control measures in the building is appended to this report. |  |  |  |  |  |  |  |  |
|  | There are a total of: |  | remotely installed amplifiers in this FAS. |  |  |  |  |  |
|  |  |  | supervised power supplies in this FAS. |  |  |  |  |  |
|  |  |  | remote sequential display units in this FAS. |  |  |  |  |  |
|  |  |  | remote annunciators in this FAS. |  |  |  |  |  |
|  |  |  | remote trouble units in this FAS. |  |  |  |  |  |
|  |  |  | stand-by batteries in this FAS. |  |  |  |  |  |
|  |  |  | remote booster/power supplies in this FAS. |  |  |  |  |  |
| List all locations where remote booster/power supplies, batteries & amplifiers are installed: |  |  |  |  |  |  |  |  |

| Date: |  | Annual Special Inspection/Audit |  |
| --- | --- | --- | --- |
| Building Name: |  | Address: |  |

| C2.1 Control Unit or Transponder Tests |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Control Unit/Transponder Field Location: |  |  |  |  |  |  |  |  |
| Control Unit/Transponder Identification: |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  | Yes | No | N/A |
| A | Power ‘on’ visual indicator operates. |  |  |  |  |  |  |  |
| B | Common visual trouble signal operates. |  |  |  |  |  |  |  |
| C | Common audible trouble signal operates. |  |  |  |  |  |  |  |
| D | Trouble signal silence switch operates. |  |  |  |  |  |  |  |
| E | Main Power supply failure trouble signal operates. |  |  |  |  |  |  |  |
| F | Ground fault tested on positive and negative initiates trouble signal. |  |  |  |  |  |  |  |
| G | Alert signal operates. |  |  |  |  |  |  |  |
| H | Alarm signal operates. |  |  |  |  |  |  |  |
| I | Automatic transfer from alert signal to alarm signal operates. |  | Time: |  |  |  |  |  |
| J | Manual transfer from alert signal to alarm signal. |  |  |  |  |  |  |  |
| K | Automatic transfer from alert to alarm signal cancel (acknowledge) operates on a two stage system. |  |  |  |  |  |  |  |
| L | Alarm signal silence inhibit function operates. |  |  |  |  |  |  |  |
| M | Alarm signal manual silence operates. |  |  |  |  |  |  |  |
| N | Alarm signal silence visual indication operates |  |  |  |  |  |  |  |
| O | Alarm signal and visible signal devices, when silenced, automatically reinitiate upon subsequent alarm. In same zone In other zone/circuit |  |  |  |  |  |  |  |
| P | Alarm signal silence automatic cut-out timer. |  | Time: |  |  |  |  |  |
| Q | Audible and visual alert signals and alarm signals programmed and operate per design and specification, or documentation as detailed in Appendix E, Description of Fire Alarm System for Inspection and Test Procedures. |  |  |  |  |  |  |  |
| R | Input circuit alarm and supervisory operation, including audible and visual indication operates. |  |  |  |  |  |  |  |
| S | Input circuit supervision fault causes a trouble indication. |  |  |  |  |  |  |  |
| T | Output circuit alarm indicators operate. |  |  |  |  |  |  |  |
| U | Output circuit supervision fault causes a trouble indication. |  |  |  |  |  |  |  |
| V | Visual indicator test (lamp test) operates. |  |  |  |  |  |  |  |
| W | Coded signal sequences operate not less than the required number of times and the correct alarm signal operates thereafter. |  |  |  |  |  |  |  |
| X | Coded signal sequences are not interrupted by subsequent alarms. |  |  |  |  |  |  |  |
| Y | Ancillary device by-pass results in trouble signal. |  |  |  |  |  |  |  |
| Z | Input circuit to output circuit operation, including ancillary device circuits for correct program operation, as per design and specification, or documentation as detailed in Appendix E, Description of Fire Alarm System for Inspection and Test Procedures. |  |  |  |  |  |  |  |
| AA | Fire alarm reset function operates. |  |  |  |  |  |  |  |
| BB | Main power to emergency power supply transfer operates. |  |  |  |  |  |  |  |
| CC | Smoke detector alarm verification (status change confirmation) verified. [Refer to Subsection 6.7.4.3, Smoke Detector Alarm Verification (Status Change Confirmation)]. |  |  |  |  |  |  |  |
| Recommended Additional Testing (not mandated by the Standard): |  |  |  |  |  | Yes | No | N/A |
| Alarm, trouble, & supervisory relays function correctly. |  |  |  |  |  |  |  |  |
| Control panel bonded to ground. |  |  |  |  |  |  |  |  |
| Is an AC disconnecting switch installed? YES NO (ULC CAN4-S524 restricts this, but some AHJ’s will accept it. A “YES” answer here must be noted in the “Remarks” section of this report.) |  |  |  |  |  |  |  |  |

| Date: |  | Annual Special Inspection/Audit |  |
| --- | --- | --- | --- |
| Building Name: |  | Address: |  |

| C2.2 Voice Communication Test |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| Location: |  |  |  |  |  |  |
| Identification: |  |  |  |  |  |  |
|  |  |  |  | Yes | No | N/A |
| A | Power ‘on’ visual indicator operates. |  |  |  |  |  |
| B | Common visual trouble signal operates. |  |  |  |  |  |
| C | Common audible trouble signal operates. |  |  |  |  |  |
| D | Trouble signal silence switch operates. |  |  |  |  |  |
| E | All-call voice paging, including visual indicator, operates. |  |  |  |  |  |
| F | Output circuits for selective voice paging, including visual indication, operates. |  |  |  |  |  |
| G | Output circuits for selective voice paging trouble operation, including visual indication, operates. |  |  |  |  |  |
| H | Microphone, including press to talk switch, operates. |  |  |  |  |  |
| I | Operation of voice paging does not interfere with initial inhibit time of alert signal and alarm signal. |  |  |  |  |  |
| J | All-call voice paging operates (on emergency power supply). |  |  |  |  |  |
| K | Upon failure of one amplifier, system automatically transfers to backup amplifier(s). |  |  |  |  |  |
| L | Circuits for emergency telephone call-in operation, including audible and visual indication operates. |  |  |  |  |  |
| M | Circuits for emergency telephones for operation, including two-way voice communication, operates. |  |  |  |  |  |
| N | Circuits for emergency telephone trouble operation, including visual indication, operates. |  |  |  |  |  |
| O | Emergency telephone verbal communication operates. |  |  |  |  |  |
| P | Emergency telephone operable or in-use tone at handset operates. |  |  |  |  |  |
| Q | While in standby mode, voice communication busses used for paging, alert signal, alarm signal, and emergency telephone communication circuits, an open circuit fault, or short circuit fault, or operation of an overcurrent protective device provided for the purpose, shall result in a specific trouble indication specific to the faulty buss. |  |  |  |  |  |
| Recommended Additional Testing (not mandated by the Standard): |  |  |  | Yes | No | N/A |
| Visual indicator test (lamp test) operates. |  |  |  |  |  |  |
| Main power to emergency power supply transfer operates. |  |  |  |  |  |  |
| Communication control enclosure bonded to ground. |  |  |  |  |  |  |
| Trouble signal on the voice communication system results in common trouble signal on the fire alarm system. |  |  |  |  |  |  |
| Dead-front panel(s) in place & as per manufacturer’s specification. |  |  |  |  |  |  |

| Date: |  | Annual Special Inspection/Audit |  |
| --- | --- | --- | --- |
| Building Name: |  | Address: |  |

| C2.3 Control Unit or Transponder Inspection |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Control Unit/Transponder Field Location: |  |  |  |  |  |  |  |  |  |  |  |
| Control Unit/Transponder Identification: |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  | Yes | No | N/A |
| A | Input circuit designations correctly identified in relation to connected field devices. |  |  |  |  |  |  |  |  |  |  |
| B | Output circuit designations correctly identified in relation to connected field devices. |  |  |  |  |  |  |  |  |  |  |
| C | Correct designations for common control functions and indicators. |  |  |  |  |  |  |  |  |  |  |
| D | Plug-in components and modules securely in place. |  |  |  |  |  |  |  |  |  |  |
| E | Plug-in cables securely in place. |  |  |  |  |  |  |  |  |  |  |
| F | Record the date, revision and version of firmware: |  |  |  |  |  |  |  |  |  |  |
|  | Date: |  | Revision: |  |  | Version: |  |  |  |  |  |
|  | Record the date, revision and version of the program software: |  |  |  |  |  |  |  |  |  |  |
|  | Date: |  | Revision: |  |  | Version: |  |  |  |  |  |
| G | Control unit/transponder is clean and free of dust and dirt. |  |  |  |  |  |  |  |  |  |  |
| H | Fuses in accordance with the manufacturer’s specification. |  |  |  |  |  |  |  |  |  |  |
| I | Control unit/transponder lock is functional. |  |  |  |  |  |  |  |  |  |  |
| J | Termination points for wiring to field devices secure. |  |  |  |  |  |  |  |  |  |  |
| Recommended Additional Visual Inspection (not mandated by the Standard): |  |  |  |  |  |  |  |  | Yes | No | N/A |
| Dead-front panel(s) in place & as per manufacturer’s specification. |  |  |  |  |  |  |  |  |  |  |  |
| Field wiring entry points for the various circuits and circuit separations are in accordance with the manufacturer’s installation instructions. |  |  |  |  |  |  |  |  |  |  |  |
| Main power supply feed wiring is in accordance with the manufacturer’s specifications. |  |  |  |  |  |  |  |  |  |  |  |
| Each control unit/transponder has been furnished with installation, operating and maintenance instructions. |  |  |  |  |  |  |  |  |  |  |  |

| Date: |  | Annual Special Inspection/Audit |  |
| --- | --- | --- | --- |
| Building Name: |  | Address: |  |

| C2.4 Power Supply Inspection |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Power Supply Field Location: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Power Supply Identification: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Circuit Disconnect Means Location: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Circuit Panel/Breaker Identification: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Yes | No | N/A |
| A | Fused in accordance with the manufacturer’s marked rating of the system. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| B | Adequate to meet the requirements of the system. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| C | Where fault isolation in power distribution riser has been provided, tests have been conducted to ensure a wire-to-wire short in the field wiring between each pair of control units or transponders, in turn, results in annunciation of the fault and continued operation outside of the shorted section confirmed. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Recommended Additional Visual Inspection (not mandated by the Standard): |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Yes | No | N/A |
| Dead-front panel(s) in place & as per manufacturer’s specification. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Ancillary devices, which are powered from the control unit or transponder, are recorded. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Power for ancillary devices is taken from a source separate from the fire alarm system control unit or transponder power supply. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Power for ancillary devices is taken from the control unit or transponder that is designed to provide such power. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Power supply cabinet (where applicable) is clean and free of dust and dirt. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| C2.5 Emergency Power Supply Test And Inspection |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Emergency Power Supply Field Location: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Emergency Power Supply Identification: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Battery Type (as installed): |  |  |  |  |  | Sealed Lead Acid Ni-Cad Lithium-Ion Wet Lead |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Battery Capacity (as installed): |  |  |  |  |  |  |  |  |  | AH |  |  |  |  |  |  |  |  |  |
| Required Building Code Alarm Operation: |  |  |  |  |  | 30 minutes 120 minutes |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | Yes | No | N/A |
| A | Correct battery type as recommended by the manufacturer. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| B | Correct battery rating as determined by battery calculations based on full system load. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| C | Battery voltage (main power “on”): |  |  |  |  |  |  |  |  |  |  |  | VDC |  |  |  |  |  |  |
| D | Battery voltage – main power “off” – FAS in supervisory condition: |  |  |  |  |  |  |  |  |  |  |  | VDC |  |  |  |  |  |  |
|  | Battery current - main power “off” – FAS in supervisory condition: |  |  |  |  |  |  |  |  |  |  |  | mA |  |  |  |  |  |  |
| E | Battery voltage – main power “off” – FAS in full load ALARM: |  |  |  |  |  |  |  |  |  |  |  | VDC |  |  |  |  |  |  |
|  | Battery current – main power “off” – FAS in full load ALARM: |  |  |  |  |  |  |  |  |  |  |  | A |  |  |  |  |  |  |
| F | Battery charging current (main power “on”): |  |  |  |  |  |  |  |  |  |  |  | mA |  |  |  |  |  |  |
| G | Inspected for physical damage. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| H | Terminals cleaned and lubricated. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| I | Terminals clamped tightly. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| J | Correct electrolyte level. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| K | Specific gravity of the electrolyte is within the battery manufacturer’s specifications. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| L | Inspected for electrolyte leakage. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| M | Adequately ventilated. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| N | Record manufacturer’s date code or in-service date: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| O | Disconnection causes trouble signal. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| P | Indicate type of test performed on a fully charged battery (select one): |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | (i) |  | Required supervisory load for 24 h followed by the required full load operation; |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | (ii) |  | Silent test using load resistor method for full duration test. (Refer to Appendix F1); |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | (iii) |  | Silent accelerated test. (Refer to Appendix F2); |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | (iv) |  | A battery capacity meter test. (Refer to Appendix F3); or |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | (v) |  | Replace the batteries with a new set having a current date code/capacity/type |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Q | Record calculated battery capacity (refer to Appendix D3.1-C). |  |  |  |  |  |  |  |  |  |  | AH |  |  |  |  |  |  |  |
| R | Record the battery terminal voltage after tests are completed. |  |  |  |  |  |  |  |  |  |  | VDC |  |  |  |  |  |  |  |
| S | Battery voltage not less than 85% of its rated capacity after tests completed. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| T | Generator provides power to the AC circuit serving the fire alarm system. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| U | Trouble condition at the emergency generator results in an audible common trouble signal and a visual indication at the required annunciator. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Recommended Additional Inspection (not mandated by the Standard): |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Generator fueled by: Diesel Natural Gas Other: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Fuel Level: |  |  |  | % of full capacity |  |  | Estimated run time: |  |  |  |  |  |  |  |  | Hours |  |  |  |

| Date: |  | Annual Special Inspection/Audit |  |
| --- | --- | --- | --- |
| Building Name: |  | Address: |  |

| C2.6 ANNUNCIATOR AND DISPLAY AND CONTROL CENTRE TEST AND INSPECTION |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Annunciator Location: |  |  |  |  |  |  |  |  |
| Annunciator Identification: |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  | Yes | No | N/A |
| A | Power “on” indicator operates. |  |  |  |  |  |  |  |
| B | Individual alarm and supervisory input zone clearly indicated and separately designated. |  |  |  |  |  |  |  |
| C | Individual alarm and supervisory input zone designation labels are properly identified. |  |  |  |  |  |  |  |
| D | Where active and supporting field devices are utilized, device labels correspond with actual field location. |  |  |  |  |  |  |  |
| E | Common trouble signal operates. |  |  |  |  |  |  |  |
| F | Visual indicator test (lamp test) operates. |  |  |  |  |  |  |  |
| G | Input wiring from control unit or transponder is supervised and of the correct type and gauge in accordance with the equipment manufacturer’s installation wiring requirements. |  |  |  |  |  |  |  |
| H | Alarm signal silence visual indicator operates. |  |  |  |  |  |  |  |
| I | Switches for ancillary functions operate as per design and specification. |  |  |  |  |  |  |  |
| J | Ancillary functions visual indicators operates. |  |  |  |  |  |  |  |
| K | Manual activation of alarm signal and indication operates. |  |  |  |  |  |  |  |
| L | Displays are visible in the installed location. |  |  |  |  |  |  |  |
| M | Operates on emergency power. |  |  |  |  |  |  |  |
| N | Multi-line sequential display operates as per Appendix C5.9 (Annunciators or Sequential Displays), where utilized. |  |  |  |  |  |  |  |
| C2.7 ANNUNCIATORS OR SEQUENTIAL DISPLAYS |  |  |  |  |  |  |  |  |
| Annunciator/Sequential Display Location: |  |  |  |  |  |  |  |  |
| Annunciator/Sequential Display Identification: |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  | Yes | No | N/A |
| A | Power “on” indicator operates. |  |  |  |  |  |  |  |
| B | Individual alarm and supervisory zone indication operates. |  |  |  |  |  |  |  |
|  | Exception: Operation of each individual alarm and supervisory zone indication gives the identical indication, or lights the identical indicators at the other annunciator(s) and sequential display(s). |  |  |  |  |  |  |  |
|  | Specify method of confirmation: |  |  |  |  |  |  |  |
|  | Minimum of one alarm zone and one supervisory zone tested per annunciator or sequential display to confirm operation. |  |  |  |  |  |  |  |
| C | Individual alarm and supervisory input zone designation labels are properly identified. |  |  |  |  |  |  |  |
| D | Where active and supporting field devices are utilized, device labels correspond with actual field location. |  |  |  |  |  |  |  |
| E | Common trouble signal operates. |  |  |  |  |  |  |  |
| F | Visual indicator test (lamp test) operates. |  |  |  |  |  |  |  |
| G | Input wiring from control unit or transponder is supervised and of the correct type and gauge in accordance with the equipment manufacturer’s installation wiring requirements. |  |  |  |  |  |  |  |
| H | Alarm signal silence visual indicator operates. |  |  |  |  |  |  |  |
| I | Switches for ancillary functions operate as per design and specification. |  |  |  |  |  |  |  |
| J | Ancillary functions visual indicators operates. |  |  |  |  |  |  |  |
| K | Manual activation of alarm signal and indication operates. |  |  |  |  |  |  |  |
| L | Displays are visible in the installed location. |  |  |  |  |  |  |  |
| C2.8 Remote Trouble Signal Unit Test And Inspection |  |  |  |  |  |  |  |  |
| Remote trouble signal unit location: |  |  |  |  |  |  |  |  |
| Remote trouble signal unit identification: |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  | Yes | No | N/A |
| A | Input wiring from control unit or transponder is supervised. |  |  |  |  |  |  |  |
| B | Visual trouble signal operates. |  |  |  |  |  |  |  |
| C | Audible trouble signal operates. |  |  |  |  |  |  |  |

| Date: |  | Annual Special Inspection/Audit |  |
| --- | --- | --- | --- |
| Building Name: |  | Address: |  |

| C2.9 Printer Test |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Printer Location: |  |  |  |  |  |  |  |  |  |  |
| Printer Identification: |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  | Yes |  | No | N/A |
| A |  | Operates as per design and specification, or in accordance with documentation provided in Appendix E. |  |  |  |  |  |  |  |  |
| B |  | Zone of each alarm initiating device is correctly printed. |  |  |  |  |  |  |  |  |
| C |  | Rated voltage is present. |  |  |  |  |  |  |  |  |
| C2.10 Operation Test for Data Communication Link |  |  |  |  |  |  |  |  |  |  |
| Control Unit/Transponder Field Location: |  |  |  |  |  |  |  |  |  |  |
| Control Unit/Transponder Identification: |  |  |  |  |  |  |  |  |  |  |
| DCL Identification: |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  | Yes | No |  | N/A |
| A | Confirm that a trouble signal is received at the control unit or transponder under an open loop fault. |  |  |  |  |  |  |  |  |  |
| B | Where fault isolation modules are installed in data communication links serving field devices, wiring shorted on the isolated side, annunciation of the fault confirmed, and then a device on the source side operated, and activation confirmed at the control unit or transponder. |  |  |  |  |  |  |  |  |  |
| C | Where fault isolation in data communication links is provided between control units or transponders and between transponders, introduce a short circuit fault and confirm annunciation of the fault and operation outside the shorted section between each pair of: |  |  |  |  |  |  |  |  |  |
|  | - Control unit to control unit |  |  |  |  |  |  |  |  |  |
|  | - Control unit to transponder |  |  |  |  |  |  |  |  |  |
|  | - Transponder to transponder |  |  |  |  |  |  |  |  |  |
| Control Unit/Transponder Field Location: |  |  |  |  |  |  |  |  |  |  |
| Control Unit/Transponder Identification: |  |  |  |  |  |  |  |  |  |  |
| DCL Identification: |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  | Yes | No |  | N/A |
| A | Confirm that a trouble signal is received at the control unit or transponder under an open loop fault. |  |  |  |  |  |  |  |  |  |
| B | Where fault isolation modules are installed in data communication links serving field devices, wiring shorted on the isolated side, annunciation of the fault confirmed, and then a device on the source side operated, and activation confirmed at the control unit or transponder. |  |  |  |  |  |  |  |  |  |
| C | Where fault isolation in data communication links is provided between control units or transponders and between transponders, introduce a short circuit fault and confirm annunciation of the fault and operation outside the shorted section between each pair of: |  |  |  |  |  |  |  |  |  |
|  | - Control unit to control unit |  |  |  |  |  |  |  |  |  |
|  | - Control unit to transponder |  |  |  |  |  |  |  |  |  |
|  | - Transponder to transponder |  |  |  |  |  |  |  |  |  |
| Control Unit/Transponder Field Location: |  |  |  |  |  |  |  |  |  |  |
| Control Unit/Transponder Identification: |  |  |  |  |  |  |  |  |  |  |
| DCL Identification: |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  | Yes | No |  | N/A |
| A | Confirm that a trouble signal is received at the control unit or transponder under an open loop fault. |  |  |  |  |  |  |  |  |  |
| B | Where fault isolation modules are installed in data communication links serving field devices, wiring shorted on the isolated side, annunciation of the fault confirmed, and then a device on the source side operated, and activation confirmed at the control unit or transponder. |  |  |  |  |  |  |  |  |  |
| C | Where fault isolation in data communication links is provided between control units or transponders and between transponders, introduce a short circuit fault and confirm annunciation of the fault and operation outside the shorted section between each pair of: |  |  |  |  |  |  |  |  |  |
|  | - Control unit to control unit |  |  |  |  |  |  |  |  |  |
|  | - Control unit to transponder |  |  |  |  |  |  |  |  |  |
|  | - Transponder to transponder |  |  |  |  |  |  |  |  |  |

| Date: |  | Annual Special Inspection/Audit |  |
| --- | --- | --- | --- |
| Building Name: |  | Address: |  |

| C5.13 Interconnection to the Fire Signal Receiving Centre |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Communicator Location: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Circuit Disconnect Means Location: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Circuit Panel/Breaker Identification: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  | Yes | No | N/A |
| A | The fire signal receiving centre transmitter is integral to the fire alarm control unit. |  |  |  |  |  |  |  |  |  |  |  |  |  |
| B | The fire signal receiving centre transmitter is located remotely from the fire alarm control unit. |  |  |  |  |  |  |  |  |  |  |  |  |  |
| C | Where an interconnection between the fire alarm control unit and a separate fire signal receiving centre transmitter is provided, a demarcation terminal box with a minimum of twelve (12) terminals is installed. |  |  |  |  |  |  |  |  |  |  |  |  |  |
| D | The demarcation terminal box is located in the same room as the fire alarm control unit it is connected to. |  |  |  |  |  |  |  |  |  |  |  |  |  |
| E | The demarcation terminal box is labeled “Fire Alarm Demarcation” and/or “Limitation D’Alarme Incendie”. |  |  |  |  |  |  |  |  |  |  |  |  |  |
| F | The conductors installed between the fire alarm control panel and the demarcation terminal box complies with Section 3.4 of CAN/ULC-S524-06. |  |  |  |  |  |  |  |  |  |  |  |  |  |
| G | Tested and confirmed operation of alarm relay. |  |  |  |  |  |  |  |  |  |  |  |  |  |
| H | Tested and confirmed operation of trouble relay. |  |  |  |  |  |  |  |  |  |  |  |  |  |
| I | Tested and confirmed operation of supervisory relay. |  |  |  |  |  |  |  |  |  |  |  |  |  |
| J | Confirm that the alarm transmission to the fire signal receiving centre is received. |  |  |  |  |  |  |  |  |  |  |  |  |  |
| K | Confirm that the supervisory transmission to the fire signal receiving centre is received. |  |  |  |  |  |  |  |  |  |  |  |  |  |
| L | Confirm that the trouble transmission to the fire signal receiving centre is received. |  |  |  |  |  |  |  |  |  |  |  |  |  |
| M | Record the name and telephone number of the fire signal receiving centre. |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Company: |  |  | Telephone: |  |  |  |  |  |  |  |  |  |  |
|  | Address: |  |  |  |  |  |  |  |  |  |  |  |  |  |
| N | Operation of the fire signal receiving centre transmitter bypass means results in a specific trouble indication at the fire alarm control unit or transponder and transmits a trouble signal to the fire signal receiving centre. |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Additional Information (not mandated by the Standard): |  |  |  |  |  |  |  |  |  |  |  | Yes | No | N/A |
| The communicator is installed in accordance with CAN/ULC-S561-13. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| The fire signal receiving centre is ULC Listed. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| The fire signal receiving centre ULC certification number is: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| The communicator is being tested in accordance with CAN/ULC-S561-13. Supporting documentation attesting to this is on site and has been reviewed. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| The ULC “Central Station Fire Protective Signalling Service” Certificate is valid. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| The ULC “Central Station Fire Protective Signalling Service” Certificate expires on: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| The last inspection noted on the Certificate occurred on: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| The communicator has been reset following completion of testing. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| The communicator has been placed back into service. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| The communicator is trouble free. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |

| Date: |  | Annual Special Inspection/Audit |  |
| --- | --- | --- | --- |
| Building Name: |  | Address: |  |

| Additional CAN/ULC-S536-04 Inspection Items |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| (ULC CAN4-S536-04 5.7) Field Devices Testing |  |  |  | Yes |  | No | N/A |
| Each device is free of damage, foreign substance & mechanically supported independent of wiring? |  |  |  |  |  |  |  |
| Each device tested while connected to control unit? |  |  |  |  |  |  |  |
| Manual Pull stations tested? |  |  |  |  |  |  |  |
| Two stage pull stations tested and functions confirmed? |  |  |  |  |  |  |  |
| Heat detectors tested to ULC CAN4-S536-04 5.7.3 |  |  |  |  |  |  |  |
| (CAN/ULC-S536-04 5.7.4) Smoke Detector Testing |  |  |  | Yes |  | No | N/A |
| Inspected for cleanliness. |  |  |  |  |  |  |  |
| Sensitivity tested (results are recorded in the Device Test Record). |  |  |  |  |  |  |  |
| Tested for Operation (results are recorded in the Device Test Record). |  |  |  |  |  |  |  |
| Status change confirmation inspected and tested. |  |  |  |  |  |  |  |
| Air duct smoke detectors tested to CAN/ULC-S436-04 5.7.4.4. |  |  |  |  |  |  |  |
| Beam type smoke detectors inspected and tested. |  |  |  |  |  |  |  |
| Flame detectors inspected and tested. |  |  |  |  |  |  |  |
| Combination (multi-criteria) detectors inspected and tested? |  |  |  |  |  |  |  |
| Automatic Detectors (other types) inspected and tested for: |  |  |  |  |  |  |  |
| - Alarm initiation |  |  |  |  |  |  |  |
| - Correct orientation so as to detect the anticipated hazard |  |  |  |  |  |  |  |
| - Sensitivity tested (results are recorded in the Device Test Record) |  |  |  |  |  |  |  |
| All tested devices are compatible with the control panel. |  |  |  |  |  |  |  |
| Exceptions are identified in the Device Test Record. |  |  |  |  |  |  |  |
| (CAN/ULC-S536-04 5.7.8.1) Water Flow Detection Devices |  |  |  |  | Yes | No | N/A |
| Tested by appropriate water flow means (time delay are recorded in the Device Test Record). |  |  |  |  |  |  |  |
| (CAN/ULC-S536-04) Supervisory Devices |  |  |  | Yes |  | No | N/A |
| Shut-off valves tested and result in Trouble Supervisory signal at the fire alarm panel. |  |  |  |  |  |  |  |
| Low Pressure supervisory device inspected and tested. |  |  |  |  |  |  |  |
| Low water supervisory device inspected and tested. |  |  |  |  |  |  |  |
| Low temperature supervisory device tested. |  |  |  |  |  |  |  |
| Each power loss (i. e. fire pump and air compressor) supervisory tested. |  |  |  |  |  |  |  |
| (CAN/ULC-S536-04 5.7.8.4) Supervisory Devices (Other Types) |  |  |  | Yes |  | No | N/A |
| Inspected and tested as per manufacturer’s requirements. |  |  |  |  |  |  |  |
| (CAN/ULC-S536-04) 5.7.9 Signaling Appliances |  |  |  | Yes |  | No | N/A |
| Individually inspected and tested for operation, proper installation, tightness, tampering/obstruction. |  |  |  |  |  |  |  |
| Intelligibility (clarity) of voice messages confirmed. |  |  |  |  |  |  |  |
| Audibility of alert, alarm and voice messages checked. |  |  |  |  |  |  |  |
| Visual signal appliances individually inspected and tested. |  |  |  |  |  |  |  |
| Combination appliances individually inspected and tested. |  |  |  |  |  |  |  |
| In-suite signal isolator modules are identified, individually inspected, and tested. |  |  |  |  |  |  |  |
| Smoke Alarms |  |  |  | Yes |  | No | N/A |
| Powered by un-switched “AC”? |  |  |  |  |  |  |  |
| Battery operated? |  |  |  |  |  |  |  |
| Batteries Replaced? |  |  |  |  |  |  |  |
| Interconnection function tested (multiple station alarms)? |  |  |  |  |  |  |  |
| Audibility of alarm sounder checked? |  |  |  |  |  |  |  |
| Visible signaling appliances tested? |  |  |  |  |  |  |  |
| Testing results and any exceptions are identified in the Device Test Record. |  |  |  |  |  |  |  |
| Testing method used: Canned Smoke Test Button Magnet |  |  |  |  |  |  |  |

| Date: |  | Annual Special Inspection/Audit |  |
| --- | --- | --- | --- |
| Building Name: |  | Address: |  |

| C2.12 Ancillary Device Circuit Test |  |  |  |
| --- | --- | --- | --- |
| Record Specific Type of Ancillary Circuit | Operation of Ancillary Circuit Confirmed |  |  |
|  | Yes | No | N/A |

Note:  The tests reported on this form do not include the actual operational test of ancillary devices except where noted.

| Date: |  | Annual Special Inspection/Audit |  |
| --- | --- | --- | --- |
| Building Name: |  | Address: |  |

C2.13 DEFICIENCIES

C2.14 RECOMMENDATIONS

| Date: |  | Annual Special Inspection/Audit |  |
| --- | --- | --- | --- |
| Building Name: |  | Address: |  |

C2.15 REMARKS

C3.  FIELD DEVICE RECORD

C3.1 FIELD DEVICE TESTING – LEGEND AND NOTES

| Date: |  | Annual Special Inspection/Audit |  |
| --- | --- | --- | --- |
| Building Name: |  | Address: |  |

| Device | Description | Type | Model No. |
| --- | --- | --- | --- |
| M | Manual Pull station |  |  |
| HD | Heat detector, restorable or non-restorable, fixed temperature (10) |  |  |
| RHD | Heat detector, restorable, rate-of-rise thermostat (10) |  |  |
| S | Ionization type system smoke detector (1, 2, 3) |  |  |
| PS | Photo-electric type system smoke detector (1, 2, 3) |  |  |
| DS(PS) | Duct smoke detector (“PS” indicates Photo-Electric Type) (1, 2, 3, 4) |  |  |
| FS | Sprinkler flow switch (5) |  |  |
| FPS | Sprinkler flow pressure switch |  |  |
| TS | Sprinkler valve supervisory tamper switch (6) |  |  |
| LA | Low Air supervisory device (7) |  |  |
| LT | Low Temperature supervisory device (8) |  |  |
| SA | Smoke alarm (single or multi-station type) |  |  |
| EOL(R) | End-of-Line Device (“R” denotes Power Supervision Relay) (12) |  |  |
| B | Bell |  |  |
| H | Horn |  |  |
| V | Visual alarm device (strobe, corridor indicator) |  |  |
| BZ(S) | Mini Buzzer ( “S” indicates “silenceable” type) |  |  |
| SP | Cone type speaker |  |  |
| HSP | Horn type speaker |  |  |
| ET | Emergency Telephone |  |  |
| AV | Combination Audible/Visual Device (i.e. Horn/Strobe Unit) |  |  |
| OD | Other Type of Detector |  |  |
| DM | Damper Motor |  |  |
| R | Relay |  |  |
| RPM | Remote Point Module (14) |  |  |
| SRIM | Single Point Remote Initiating Module (14) |  |  |
| DRIM | Dual Input Remote Initiating Module (14) |  |  |
| SCIM | Signal Circuit Isolation Module (14) |  |  |
| SCRM | Signal Circuit Remote Module (14) |  |  |
| RRM | Remote Relay Module (14) |  |  |
| RPIM | Remote Point Isolator Module (14) |  |  |
| AD | Other Ancillary Device (11) |  |  |
| HTC | Heat Trace Controller |  |  |

- NOTES:

- Smoke detector sensitivity measurement should be recorded in the “Remarks” column of the Individual Device Test Record.  Analog smoke detectors may report their obscuration level (sensitivity) to the fire alarm’s common control.  This information should be retrieved and recorded in the “Remarks” column.

- Smoke detector cleaning or replacement date should also be recorded in the “Remarks” column.

- Status change, including time delay (where applicable), should be recorded in the “Remarks” column.

- Duct smoke detector pressure differential should be confirmed and recorded in the “Remarks” column.  Detector tubes must be pulled and their alignment confirmed if results indicate any abnormalities.  Record any discrepancies in the “Remarks” column.

- Time delay setting of water flow switch should be recorded in the “Remarks” column.

- Sprinkler supervisory switches should cause a “trouble” condition to be annunciated.  This should be a latching type trouble (or “supervisory trouble”) only restorable by pressing “Reset” on the fire alarm control panel.  Exceptions must be noted in “Comments”.

- Upper and lower pressure setting of supervisory devices should be recorded in the “Remarks” column.

- Low temperature setting should be recorded in the “Remarks” column.

- Identify the specific ancillary devices in the “Remarks” column.

- Where possible, identify the date a fire detector is changed.  If housing discolouration is noted, attempt to identify the source and note the date of manufacture.  Heat detectors whose labels are missing, faded and unreadable, or painted are considered failed and require replacement.  This information should be noted in the “Remarks” column.

- Identify correct field device operation (e.g., alarm, trouble, supervisory, annunciation indication).

- Identify zone, circuit number, or address.

- Identify conventional field device locations.

- Identify active field device and supporting field device, data communication link (DCL), address and location.

- Test and confirm conventional field device supervision of wiring.

- Confirm field device free of damage.

- Confirm field device free of foreign substance.

- Confirm field device mechanically supported independently of the wiring.

- Confirm field device protective dust shields or covers removed.

- “Correctly Installed” refers to the version of CAN/ULC-S524, Standard for Installation of Fire Alarm Systems, applicable at the time of installation of the device being tested.

C3.2  INDIVIDUAL DEVICE RECORD

| Date: |  | Annual Special Inspection/Audit |  |
| --- | --- | --- | --- |
| Building Name: |  | Address: |  |

| Column Legend |  |  |  |
| --- | --- | --- | --- |
| A B C | Correctly installed Unit requires service, repair, missing, or cleaning Alarm operation confirmed | D E F G | Annunciator indication confirmed Circuit number or address Smoke detector sensitivity Output circuit operation confirmed |

“” Yes - Acceptable    “X” No – Unacceptable (Explain NO answers in Remarks)    “-” Not Applicable

| Location | Device | A | B | C | D | E | F | G | Remarks |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |

Note:  Confirmation of wiring supervision to each individual device is only required during an

initial inspection and test or verification, and is not required at the annual test.

| Insert Logo Here | Service Company Information (Address, Telephone, & Contact Information |  | Emergency Lighting Unit Tests |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  | Date of Service: |  | Last Service Date: |  |  |  |
|  |  |  | Monthly | Annual |  |  | Special Inspection |  |
| Building Name: |  |  | Contact Person: |  |  | Phone: |  |  |
|  |  |  |  |  |  | Fax: |  |  |
| Address: |  |  | Owner/Strata Number: |  |  | Phone: |  |  |
|  |  |  |  |  |  | Fax: |  |  |
| City: |  | Postal Code: |  |  |  |  |  |  |

| Monthly Inspection and Tests |  |  |  | Annual Tests |  |
| --- | --- | --- | --- | --- | --- |
| A | Pilot lights are functioning? | D | Battery surface clean and dry? | G | Test to ensure lights function for a duration equal to design criteria? |
| B | Terminal connections clean? | E | Electrolyte level and specific gravity, OK? | H | Test charging conditions for voltage & current recovery period to ensure charging system is functioning. |
| C | Terminal clamps clean and tight? | F | Proper light function - power loss? |  |  |

“” - Yes (Acceptable)    “X” - No (Unacceptable)    (“NO” answers explained in “Remarks/Comments”)

| Location of Unit | Monthly Inspection and Tests |  |  |  |  |  | Annual Tests |  | Times |  | Voltage/ Size | Comments |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | A | B | C | D | E | F | G | H | On | Off |  |  |

| The information on this form (and in the documents attached here-to) attest to the fact that the equipment listed here-in was tested/inspected in conformance with applicable codes, bylaws, standards, and the manufacturer’s requirements by a qualified technician. The equipment was left in an operational condition except as noted in the spaces marked “comments”. This document has been provided to the building owner’s representative who has acknowledged receipt of same below. A copy should be maintained on the premises for examination by the Fire Marshal or Inspector at their request. |  |  |  |
| --- | --- | --- | --- |
| Company Name |  |  |  |
| Technician Conducting Testing | Certification Number/Stamp | Date | Technician Signature |

Emergency Lighting Unit Tests (Continued)

| Date: |  |  |  |
| --- | --- | --- | --- |
| Building Name: |  | Address: |  |

| Monthly Inspection and Tests |  |  |  | Annual Tests |  |
| --- | --- | --- | --- | --- | --- |
| A | Pilot lights are functioning? | D | Battery surface clean and dry? | G | Test to ensure lights function for a duration equal to design criteria? |
| B | Terminal connections clean? | E | Electrolyte level and specific gravity, OK? | H | Test charging conditions for voltage & current recovery period to ensure charging system is functioning. |
| C | Terminal clamps clean and tight? | F | Proper light function - power loss? |  |  |

“” - Yes (Acceptable)    “X” - No (Unacceptable)    (“NO” answers explained in “Remarks/Comments”)

| Location of Unit | Monthly Inspection and Tests |  |  |  |  |  | Annual Tests |  | Times |  | Voltage/ Size | Comments |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | A | B | C | D | E | F | G | H | On | Off |  |  |

Remarks/Comments

| Insert Logo Here | Service Company Information (Address, Telephone, & Contact Information |  | Building Sprinkler Systems Tests |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  | Date of Service: |  | Last Service Date: |  |  |  |
|  |  |  | Daily | Weekly | Monthly |  |  | Quarterly |
|  |  |  | Semiannual | Annual | Third Year |  |  | Fifth Year |
| Building Name: |  |  | Contact Person: |  |  | Phone: |  |  |
|  |  |  |  |  |  | Fax: |  |  |
| Address: |  |  | Owner/Strata Number: |  |  | Phone: |  |  |
|  |  |  |  |  |  | Fax: |  |  |
| City: |  | Postal Code: | Central Station: |  |  | Phone: |  |  |
|  |  |  |  |  |  | Fax: |  |  |

Summary of Tests in accordance with the BC Fire Code and referenced documents.

| System | #1 | #2 | #3 | #4 | #5 |
| --- | --- | --- | --- | --- | --- |
| Wet |  |  |  |  |  |
| Dry pipe partial test |  |  |  |  |  |
| Dry pipe full flow test |  |  |  |  |  |
| Deluge |  |  |  |  |  |
| Pre-action |  |  |  |  |  |
| Other |  |  |  |  |  |
| Area of coverage |  |  |  |  |  |
| Size (gallons) |  |  |  |  |  |
| Manufacturer |  |  |  |  |  |
| System Water Pressure |  |  |  |  |  |
| Supply Water Pressure |  |  |  |  |  |
| System Air Pressure |  |  |  |  |  |
| Trip Pressure |  |  |  |  |  |
| Trip Time |  |  |  |  |  |
| System | #6 | #7 | #8 | #9 | #10 |
| Wet |  |  |  |  |  |
| Dry pipe partial test |  |  |  |  |  |
| Dry pipe full flow test |  |  |  |  |  |
| Deluge |  |  |  |  |  |
| Pre-action |  |  |  |  |  |
| Other |  |  |  |  |  |
| Area of coverage |  |  |  |  |  |
| Size (gallons) |  |  |  |  |  |
| Manufacturer |  |  |  |  |  |
| System Water Pressure |  |  |  |  |  |
| Supply Water Pressure |  |  |  |  |  |
| System Air Pressure |  |  |  |  |  |
| Trip Pressure |  |  |  |  |  |
| Trip Time |  |  |  |  |  |

| Yes | No | Visual Pre-Inspection Check |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  | Compressor Manufacturer/Model No.: |  |  |  | Date of last compressor service: |  |  |
|  |  | Designer: |  |  | Engineer: |  |  |  |
|  |  | Corrosion evident? Sprinkler Heads Joints Hangers Supply/Riser/Distribution Piping Valves |  |  |  |  |  |  |
|  |  | Corrosion is: Minor Moderate Severe Condition of heat tracing/insulation: Good Fair Poor NA |  |  |  |  |  |  |
|  |  | Replacement of affected components is indicated. (“Yes” answer detailed in remarks section) |  |  |  |  |  |  |
|  |  | Remarks concerning the system have been made? (Please refer to the Comments/Remarks section of this report.) |  |  |  |  |  |  |

| The information on this form (and in the documents attached here-to) attest to the fact that the equipment listed here-in was tested/inspected in conformance with applicable codes, bylaws, standards, and the manufacturer’s requirements by a qualified technician. The equipment was left in an operational condition except as noted in the spaces marked “comments”. This document has been provided to the building owner’s representative who has acknowledged receipt of same below. A copy should be maintained on the premises for examination by the Fire Marshal or Inspector at their request. |  |  |  |
| --- | --- | --- | --- |
| Company Name |  |  |  |
| Technician Performing Test | Certification Number/Stamp | Date | Technician Signature |

Building Sprinkler Systems Tests (Continued)

| Date: |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| Building Name: |  |  |  | Address: |  |
| Important: All daily, weekly, monthly, and quarterly inspection and testing items on this form shall be done during the Annual Inspection. Exceptions must be documented in the “Remarks/Comments” section of this report. Please attach testing data sheets for each system tested. |  |  |  |  |  |
| System Number: |  |  |  |  |  |

“” = Yes - Tested correctly    “X” = No - Did not test correctly (NO answers are detailed in “Comments/Remarks”)     “NA” = Not applicable

| Sprinkler System Inspection |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
|  | Daily / weekly if low temperature alarms are installed. |  |  |  | Oil level in normal range on air compressor? |
|  | (a) Enclosures - dry-pipe or deluge valves maintaining 40F/4C? |  |  |  | Condition of oil in sight glass? Clean Cloudy Dirty |
|  | (b) Heat trace controllers power “on”. |  |  |  | Filter checked? Replacement required? Yes No NA |
|  | (c) Is heat trace controller in “trouble”? Yes No |  |  |  | Belt checked for proper tension? Condition? Good Worn |
|  | Weekly |  |  |  | Inspect electrically supervised valves? |
|  | Relief port for reduced pressure & backflow prevention assemblies |  |  |  | Alarm devices inspected to verify they are free from physical |
|  | is free from discharge? |  |  |  | damage? |
|  | Weekly and Monthly Inspection Items |  |  |  | Pressure regulating control valves shall be inspected. |
|  | Gauges on dry, pre-action and deluge systems in good condition? |  |  |  | Sprinkler pressure regulating & control valves shall be inspected. |
|  | Inspect air pressure and water pressure? |  |  |  | Fire department connection? |
|  | Control valves (and isolation valves on backflow prevention devices): |  |  |  | Annual inspection items. |
|  | (a) in correct (open or closed) position? |  |  |  | Buildings - prior to freezing weather? |
|  | (b) Sealed, locked or supervised and accessible? |  |  |  | Hangers and seismic braces inspected from floor level? |
|  | (c) Free from external leaks? |  |  |  | Pipe and fittings shall be inspected from floor level? |
|  | (d) Provided with appropriate wrenches? |  |  |  | Sprinklers shall be inspected from floor level? |
|  | Alarm valve free from damage, trim in correct position, and no leakage? |  |  |  | Spare sprinklers shall be inspected? |
|  | Quarterly Inspection Items (in addition to above) |  |  |  | Interior of dry pipe valve shall be inspected at time of trip test? |
|  | Pre-action and deluge valves inspected externally & free from |  |  |  | Pre-action/deluge valves shall be inspected internally? |
|  | damage? |  |  |  | Interior of dry-pipe , pre-action, deluge valves internal inspection? |
|  | Electrical components in service? |  |  |  | Heat Tracing - Check all connections tight, clamped & undamaged. |
|  | Gauges wet pipe in good condition and normal water pressure |  |  |  | Check heat trace controller for trouble and ground fault response. |
|  | is being maintained? |  |  |  | Check heat trace controller interconnection to fire alarm system. |
|  | Dry pipe valve/quick opening devices shall be inspected externally. |  |  |  | Fifth year inspection items. |
|  | Backflow prevention assemblies shall be inspected (locked or |  |  |  | Alarm valves & strainers, filters and restriction orifices passed |
|  | properly supervised by an acceptable electrical means). |  |  |  | internal inspection? |
|  | Control valves shall be inspected. |  |  |  | Pre-action/deluge valve and their associated strainers, filters and |
|  | Alarm valves shall be inspected externally. |  |  |  | restriction orifices pass internal inspection? |
|  | Hydraulic name plate is properly affixed to the sprinkler riser? |  |  |  | Dry pipe valves/quick opening devices internally inspect strainers, |
|  | Date on Label: |  |  |  | filters & orifices? |
|  | Heat Tracing - check pipe insulation for cuts or abrasions. |  |  |  | Check Valves internally inspected and all parts operate properly, |
|  | Check exposed cable/connectors for chaffing, cuts, or abrasions. |  |  |  | move freely and are in good condition? |
|  |  |  |  |  | Interior of dry-pipe , pre-action, deluge valves internal inspection? |

| Sprinkler System Testing |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | Quarterly Tests |  |  |  | Annual Testing |  |  |  |  |
|  | Water flow alarms passed tests? |  |  |  | Are all sprinklers in service dated 1920 or later? |  |  |  |  |
|  | Control valves opened until spring or torsion is felt in the rod? |  |  |  | Fast Response sprinklers in service for less than 20 yrs |  |  |  |  |
|  | Valve supervisory switches indicate movement? |  |  |  | If “NO” test sample now and every 10 years? |  |  |  |  |
|  | Low air pressure alarms tested in as per mfg’s requirements? |  |  |  | Record anti-freeze Specific Gravity: |  |  |  |  |
|  | Pre-action/deluge valves (supervised) priming water tested? |  |  |  | All control valves operated thru full range and returned to normal? |  |  |  |  |
|  | Alarm device, test on dry pipe, pre-action or deluge system using |  |  |  | Pressure regulating valve shall pass a full flow test. |  |  |  |  |
|  | bypass? |  |  |  | Backflow prevention assemblies have been tested by an agency |  |  |  |  |
|  | Inspectors test connection opened? (wet pipe when not freezing) |  |  |  | acceptable to the local authority? Date: |  |  |  |  |
|  | Bypass connection opened? (wet pipe, dry pipe, pre-action and |  |  |  | Forward flow test has been conducted. |  |  |  |  |
|  | deluge systems when not freezing) |  |  |  | Forward Flow Test results are recorded on the backflow test report? |  |  |  |  |
|  | Dry pipe valves/Quick opening devices (supervised) priming water |  |  |  | Standard sprinklers less than 50 yrs old. If “no” has a sample |  |  |  |  |
|  | tested for compliance with manufacturers’ instructions? |  |  |  | been tested within 10yrs, If “no” test sample now and every 10yrs. |  |  |  |  |
|  | Quick opening devices passed test? |  |  |  | Low temperature alarms in dry pipe, pre-action and deluge |  |  |  |  |
|  | Main drain test shall be conducted on each system riser. |  |  |  | valve enclosure passed test? |  |  |  |  |
|  | Record Static pressure: |  | PSIG KPAG |  | Main Drain test shall be conducted on each system riser. |  |  |  |  |
|  | Residual pressure: |  | PSIG KPAG |  | Record Static pressure: |  |  | PSIG KPAG |  |
|  |  |  |  |  | Residual pressure: |  |  | PSIG KPAG |  |
|  |  |  |  |  | Are results comparable to previous tests? |  |  |  |  |

Building Sprinkler Systems Tests (Continued)

| Date: |  |  |  |
| --- | --- | --- | --- |
| Building Name: |  | Address: |  |

| Sprinkler System Testing Continued: |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | Pre-action and deluge valve full flow trip test: (Note: Except |  |  |  |  |  |  | Auto air maintenance devices on dry pipe & pre-action passed |  |  |  |
|  | where water cannot be discharged, test all systems simultaneously.) |  |  |  |  |  |  | test? |  |  |  |
|  | Water discharge from all nozzles unimpeded? |  |  |  |  |  |  | All sprinkler pressure regulating control valves passed full flow |  |  |  |
|  | Pressure reading at hydraulically most remote nozzle: |  |  |  |  |  |  | test? |  |  |  |
|  |  |  | PSIG KPAG |  |  |  |  | Dry-pipe full flow trip test (to be done every 3rd year): |  |  |  |
|  | Residual pressure reading at valve: |  |  |  |  | PSIG KPAG |  | Was water delivered to inspectors test connection? |  |  |  |
|  | Was flow observed? |  |  |  |  |  |  | Initial air pressure: |  | PSIG KPAG |  |
|  | Are above readings comparable to design values? |  |  |  |  |  |  | Water pressure: |  | PSIG KPAG |  |
|  | Manual activation devices passed test? |  |  |  |  |  |  | Trip air pressure: |  | PSIG KPAG |  |
|  | Automatic air pressure maintenance devices passed test? |  |  |  |  |  |  | Tripping time: |  | Seconds |  |
|  | Dry pipe valve partial flow trip test: |  |  |  |  |  |  | Date of trip test (from records on site) was: |  |  |  |
|  | Initial air pressure: |  |  |  | PSIG KPAG |  |  | Tests to be done every fifth year: |  |  |  |
|  | Water pressure: |  |  |  | PSIG KPAG |  |  | Extra High, Very Extra High and Ultra High Temp sprinklers |  |  |  |
|  | Trip air pressure: |  |  |  | PSIG KPAG |  |  | tested? |  |  |  |
|  | Tripping time: |  |  |  | Seconds |  |  | Gauges checked against calibrated gauge or replaced? |  |  |  |
|  | Are the results comparable to previous test? |  |  |  |  |  |  | Date of service (from records on site) was: |  |  |  |
|  | Post indicator valves opened until spring or torsion is felt in rod. |  |  |  |  |  |  | Are above results comparable to previous tests? |  |  |  |

| Sprinkler System Maintenance Items |  |  |  |
| --- | --- | --- | --- |
|  | Regular Maintenance Items |  | Failure to flush yard piping or surrounding public mains |
|  | If sprinklers have been replaced, were they proper replacements? |  | following new installation or repairs? |
|  | Air leaks in dry-pipe system resulting in air pressure loss more than |  | Record of broken mains in the vicinity? |
|  | 10 psi/week repaired? |  | Abnormally frequent false tripping of dry-pipe valves? |
|  | Dry-pipe systems being maintained in dry condition? |  | System is returned to service after an extended period of |
|  | If any of the following were discovered, was an obstruction |  | non-service? |
|  | investigation conducted and the system flushed? Yes No |  | There is reason to believe the system contains sodium silicate? |
|  | 1. Defective intake screen for pumps taking suction from open |  | Annual Maintenance Items |
|  | sources? |  | Operating stem of all OS&Y valves lubricated, completely |
|  | 2. Obstructive material discharged during water flow tests? |  | closed. and reopened? |
|  | 3. Foreign materials found in dry-pipe valves, check valves or |  | Interior of dry-pipe, pre-action and deluge valves cleaned? |
|  | pumps? |  | Low points drained in dry pipe, pre-action & deluge systems |
|  | 4. Heavy discoloration of water during drain test or plugging of |  | prior to freezing weather? |
|  | inspectors test connection? |  | Sprinklers and spray nozzles protecting commercial cooking |
|  | 5. Plugging of sprinklers found during activation or alteration? |  | equipment and ventilating systems replaced except for bulb- |
|  | 6. Plugging found in piping dismantled during alterations? |  | type which show no sign of grease buildup? |

Remarks/Comments:

| Insert Logo Here | Service Company Information (Address, Telephone, & Contact Information |  |  |  | Building Stand-pipe & Hose Systems Tests |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  |  |  | Date of Service: |  | Last Service Date: |  |  |  |  |
|  |  |  |  |  | System in service on inspection? YES NO |  | Fire Department Connection? YES NO |  |  |  |  |
|  |  |  |  |  | Control valves locked or supervised? YES NO |  | Flow switch installed? YES NO |  |  |  |  |
|  |  |  |  |  | Fire Pump installed? YES NO |  | Jockey Pump installed? YES NO |  |  |  |  |
| Building Name: |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  | Pressure regulating device present? YES NO |  | Hose nozzles in place? YES NO |  |  |  |  |
| Address: |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  | Length of hose provided: |  |  |  | meters feet |  |  |
| City: |  |  | Postal Code: |  | Hose is: Lined Unlined |  |  |  |  |  |  |
|  |  |  |  |  | Supply water pressure: |  |  |  |  | PSIG KPAG |  |
|  |  |  |  |  | System water pressure: |  |  |  |  | PSIG KPAG |  |
| Contact Person: |  | Phone: |  |  | Central Station: |  |  | Phone: |  |  |  |
|  |  | Fax: |  |  |  |  |  | Fax: |  |  |  |
| Owner/Strata Number: |  | Phone: |  |  | Management Company: |  |  | Phone: |  |  |  |
|  |  | Fax: |  |  |  |  |  | Fax: |  |  |  |
|  |  |  |  |  | System Class: I II III |  |  |  |  |  |  |

| Yes | No | Owners Section: |
| --- | --- | --- |
|  |  | Is the building fully sprinklered? |
|  |  | Is the building occupied? |
|  |  | Has the occupancy classification & hazard of contents remained the same? |
|  |  | Are all existing fire protection systems in service? |
|  |  | Have modifications or renovations been done since the last inspection? |
|  |  | Have any system devices (including alarms) been actuated since the last inspection? |

“” = Yes - Tested correctly    “X” = No - Did not test correctly (NO answers are detailed in “Comments/Remarks”)     “NA” = Not applicable

| Inspection Items |  |  |  |
| --- | --- | --- | --- |
|  | Daily - Weekly |  | Hose Rack Pressure Reducing Valves: |
|  | Enclosures drypipe valves maintaining 4C or 40degF? |  | Hand wheel is not broken or missing? |
|  | Check relief port on pressure reducer valves are not leaking? |  | No leaks are present? |
|  | Control valves inspected for condition (“Open” or “Closed” as required). |  | Piping: |
|  | Gauges on dry system (no low pressure alarm)? |  | Piping undamaged? |
|  | Quarterly |  | Control valves undamaged? |
|  | Backflow Prevention Assembly - OS&Y valves are in the normal “Open” |  | Supervisory devices undamaged? |
|  | position? |  | No visible obstructions? |
|  | Reduced pressure assembly valves inspected for leaks or corrosion? |  | No missing or damaged pipe support devices? |
|  | Tamper switches inspected (covers secured, leaks or corrosion)? |  | Hose Connections/Valves: |
|  | Gauges to ensure good condition and normal pressure? |  | Cap in place and not damaged? |
|  | Components of standpipe system inspected? |  | Fire hose connection undamaged? |
|  | Fire department Siamese connection checked (covers in place & secure)? |  | Valve handles in place? |
|  | Hose Connection Pressure Reducing Valves: |  | Cap gaskets in place and in good condition? |
|  | Hand wheel is not broken or missing? |  | Valves not leaking? |
|  | Outlet hose threads are undamaged? |  | Restricting orifice in place? |
|  | No leaks are present? |  | Manual, semiautomatic, or dry standpipe valve operates |
|  | Reducer and cap are not missing? |  | smoothly? |

| The information on this form (and in the documents attached here-to) attest to the fact that the equipment listed here-in was tested/inspected in conformance with applicable codes, bylaws, standards, and the manufacturer’s requirements by a qualified technician. The equipment was left in an operational condition except as noted in the spaces marked “comments”. This document has been provided to the building owner’s representative who has acknowledged receipt of same below. A copy should be maintained on the premises for examination by the Fire Marshal or Inspector at their request. |  |  |  |
| --- | --- | --- | --- |
| Technician Performing Test | Certification Number/Stamp | Date | Technician Signature |

Building Standpipe and Hose Systems Testing (Continued)

| Date: |  |  |  |
| --- | --- | --- | --- |
| Building Name: |  | Address: |  |

“” = Yes - Tested correctly    “X” = No - Did not test correctly (NO answers are detailed in “Comments/Remarks”)     “NA” = Not applicable

| Inspection Items |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
|  | Annually |  |  |  | Hose Storage Devices: |
|  | Hoses: |  |  |  | Operates easily? |
|  | Free from mildew, cuts and deterioration? |  |  |  | Devices undamaged, unobstructed? |
|  | Couplings of compatible threads and undamaged? |  |  |  | Hose properly racked or rolled? |
|  | Gaskets in place and in good condition? |  |  |  | Nozzle clips in place and nozzles contained? |
|  | Hose(s) connected? |  |  |  | Will racks swing out of the cabinet at least ninety (90) degrees? |
|  | Hose hydrostatic test dates are noted on page numbers: |  |  |  | Storage Cabinets: |
|  | Nozzles: |  |  |  | Glass break device in place? |
|  | Nozzles & gaskets in place and in good condition? |  |  |  | Cabinets accessible and identified? |
|  | No visible obstructions? |  |  |  | All parts (valves, hoses and fire extinguishers) accessible? |
|  | Nozzles operate smoothly? |  |  |  | Adequate heat available to areas where wet pipe is located? |
|  | Nozzle is intact with no parts missing? |  |  |  | No visible obstructions? |
|  | Full operation of adjustments (such as pattern selection)? |  |  |  | Cabinets have no corroded or damaged parts? |
|  |  |  |  |  | Cabinets easy to fully open? |
|  |  |  |  |  | Door glazing in good condition? |
|  |  |  |  |  | Latches functional (including break-glass type)? |

| Testing Items |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
|  | Quarterly |  |  |  | Hose connection pressure reducing valves partial flow test. |
|  | Water flow alarms passed test and provide correct annunciation? |  |  |  | Hose rack assembly pressure reducing valve partial flow test. |
|  | Valve supervisory switches indicate movement? |  |  |  | Backflow prevention assembly shall be tested at the design flow. |
|  | Control valves shall be opened until spring or torsion is felt in the rod? |  |  |  | 5 Year Tests |
|  | Jockey pump operational and in good condition? |  |  |  | Hose Connection Pressure Reducing Valve passed flow test? |
|  | Valve supervisory switches tested? |  |  |  | Hose Rack Assembly Pressure Reducing Valve passed flow test? |
|  | Annual Tests |  |  |  | Hydrostatic test at not less than 13.8 bar (200 psi) for 2 hours or |
|  | Control valves shall be operated through its full range and returned to |  |  |  | at 3.4 bar (50 psi) in excess of maximum pressure? |
|  | normal. |  |  |  | Flow Test - by flowing the required volume of water at design |
|  | Main Drain test shall be conducted on each system riser. |  |  |  | pressure to the hydraulically most remote hose connection? |
|  | Static pressure: |  | PSIG KPAG |  | Check-valves internally inspected and all parts operate properly, |
|  | Residual pressure: |  | PSIG KPAG |  | move freely, and are in good condition? |
|  | Are results comparable to previous tests? |  |  |  | Pressure control valve passed test? |
|  |  |  |  |  | Gauges tested and calibrated or replaced? |

| Maintenance Items |  |  |  |
| --- | --- | --- | --- |
|  | Annually |  | Control Valves - OS&Y stems shall be lubricated? |
|  | Hose nozzles - open and close and lubricate if necessary. |  | Hose connections? |
|  | Swing out Racks - lubricate and ensure proper operation. |  | Low points in dry systems drained prior to freezing weather? |
|  | Hoses re-racked? |  | 5 Year Tests |
|  | Interior of dry pipe valve cleaned? |  | Check valves internally inspected and operating properly? |

|  | Standpipe Hydrostatic and Flow Test Results (to be completed every five years) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | Date of last hydro-test: |  |  |  |  |  |  | Date of last flow test: |  |  |  |  |  |  |  |
|  | Start Time: |  |  | End Time: |  |  |  | Start Time: |  |  | End Time: |  |  |  |  |
|  | Initial Test Pressure: |  |  | Bar (PSI) |  |  |  | Static Pressure: |  |  | Bar (PSI) |  |  |  |  |
|  | End Test Pressure: |  |  | Bar (PSI) |  |  |  | Residual Pressure:: |  |  | Bar (PSI) |  |  |  |  |
|  |  |  |  |  |  |  |  | Pitot Pressure: |  |  | Bar (PSI) |  |  |  |  |
|  |  |  |  |  |  |  |  | Nozzle Diameter: |  |  | cm inches |  |  |  |  |
|  |  |  |  |  |  |  |  | Flow Rate: |  |  | liters/min gallons/min |  |  |  |  |
|  | Notes: - Flow tests are to be conducted from the hydraulically most remote standpipe outlet. - For Class I or III systems, the minimum flow should be 1893 liters/min (500 gallons/min) at a residual pressure of 6.9 bar (100 psi) - For Class II systems, the minimum flow should be 379 liters/min (100 gallons/min) at a residual pressure of 4.5 bar (65 psi) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Comments/Remarks: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |

| Insert Logo Here | Service Company Information (Address, Telephone, & Contact Information |  | Extinguisher/Fire Hose Unit Tests |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  | Date of Service: |  | Last Service Date: |  |  |  |
|  |  |  | Monthly | Annual |  |  | Special Inspection |  |
| Building Name: |  |  | Contact Person: |  |  | Phone: |  |  |
|  |  |  |  |  |  | Fax: |  |  |
| Address: |  |  | Owner/Strata Number: |  |  | Phone: |  |  |
|  |  |  |  |  |  | Fax: |  |  |
| City: |  | Postal Code: |  |  |  |  |  |  |

| Column Legend |  |  |  |
| --- | --- | --- | --- |
| Mfg Date Svc Date | Date of Manufacture (year only) Last Major Service Date (year only) | Major Service Performed |  |
|  |  | R M H | Recharge Internal Maintenance Hydrostatic Test |

“” = Yes - Acceptable      “X” = No - Not Acceptable (Explain “NO” answers in comments).

| EXTINGUISHERS/HOSES |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| LOCATION | SIZE / TYPE | SERIAL # | Mfg Date | Svc Date | R M H | T | REMARKS |

Comments/Notations:

| The information on this form (and in the documents attached here-to) attest to the fact that the equipment listed here-in was tested/inspected in conformance with applicable codes, bylaws, standards, and the manufacturer’s requirements by a qualified technician. The equipment was left in an operational condition except as noted in the spaces marked “comments”. This document has been provided to the building owner’s representative who has acknowledged receipt of same below. A copy should be maintained on the premises for examination by the Fire Marshal or Inspector at their request. |  |  |  |
| --- | --- | --- | --- |
| Company Name |  |  |  |
| Technician Performing Test | Certification Number/Stamp | Date | Technician Signature |

Extinguisher/Fire Hose Unit Tests (Continued)

| Date: |  |  |  |
| --- | --- | --- | --- |
| Building Name: |  | Address: |  |

| Column Legend |  |  |  |
| --- | --- | --- | --- |
| Mfg Date Svc Date | Date of Manufacture (year only) Last Major Service Date (year only) | Major Service Performed |  |
|  |  | R M H | Recharge Internal Maintenance Hydrostatic Test |

“” = Yes - Acceptable      “X” = No - Not Acceptable (Explain “NO” answers in comments).

| EXTINGUISHERS/HOSES |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| LOCATION | SIZE / TYPE | SERIAL # | Mfg Date | Svc Date | R M H | T | REMARKS/COMMENTS |

Comments/Notations:

| Insert Logo Here | Service Company Information (Address, Telephone, & Contact Information |  | Building Fire Pump Tests |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  | Date of Service: |  | Last Service Date: |  |  |  |
|  |  |  | Daily | Weekly | Monthly |  |  | Quarterly |
|  |  |  | Semiannual | Annual | Third Year |  |  | Fifth Year |
| Building Name: |  |  | Contact Person: |  |  | Phone: |  |  |
|  |  |  |  |  |  | Fax: |  |  |
| Address: |  |  | Owner/Strata Number: |  |  | Phone: |  |  |
|  |  |  |  |  |  | Fax: |  |  |
| City: |  | Postal Code: | Central Station: |  |  | Phone: |  |  |
|  |  |  |  |  |  | Fax: |  |  |

| NAME PLATE INFORMATION: |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| PUMP |  |  | MOTIVATOR |  |  |  |  |  |  |  |
| Make: |  |  | Type: | Diesel Electric Other: |  |  |  |  |  |  |
| Model: |  |  | Make: |  |  | Serial Number: |  |  |  |  |
| Serial Number: |  |  | Model: |  |  | Size: |  |  |  | HP |
| Capacity @ 100%: |  | GPM LPM | Voltage: |  |  | Full Load Current: |  |  |  | Amps |
| Rated Head @ 100%: |  | PSIG KPAG | Enclosure: |  |  | Rated Speed: |  |  |  | RPM |
| Capacity @ 150%: |  | GPM LPM | No. of Cylinders: |  |  |  |  |  |  |  |
| Rated Head @ 150% |  | PSIG KPAG | CONTROLLER |  |  |  |  |  |  |  |
| Shut-off Head: |  | PSIG KPAG | Make: |  |  |  | Serial Number: |  |  |  |
| Supply Pressure: |  | PSIG KPAG | Model: |  |  |  | Transfer Switch? |  | Yes No |  |

NOTE:  The pump manufacturer may specify additional testing requirements.  The printed maintenance and testing guide must be followed.

“” = Yes - Tested correctly    “X” = No - Did not test correctly (NO answers are detailed in “Comments/Remarks”)     “NA” = Not applicable

| FIRE PUMP INSPECTION ITEMS |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | WEEKLY INSPECTION ITEMS |  |  |  |  |  |  | Battery terminals clean, tight and free from corrosion |  |  |
|  | Fire Pump Room/Enclosure |  |  |  |  |  |  | All alarm & trouble indicators are off (activate visual lamp test function) |  |  |
|  | Heated to maintain temperature above 4C / 40deg |  |  |  |  |  |  | Exhaust System |  |  |
|  | Suction and discharge pressure gauges free from damage |  |  |  |  |  |  | Inspected for leakage |  |  |
|  | Ventilation louvers are unobstructed and free to operate |  |  |  |  |  |  | Condensation trap drained |  |  |
|  | System Piping and Valve Condition |  |  |  |  |  |  | Electrical System Conditions |  |  |
|  | Pump suction, discharge and bypass valves in normal position |  |  |  |  |  |  | Controller power light on |  |  |
|  | Inspect associated piping for leaks |  |  |  |  |  |  | Transfer switch normal, pilot light illuminated |  |  |
|  | Suction line pressure normal? |  |  | PSIG KPAG |  |  |  | Isolating switch closed - standby (emergency) source |  |  |
|  | System line pressure normal? |  |  | PSIG KPAG |  |  |  | Reverse phase alarm pilot light off or normal phase rotation pilot lamp on |  |  |
|  | Suction reservoir full? |  |  |  |  |  |  | Oil level in normal (check sight glass) |  |  |
|  | Wet pit suction screens are unobstructed and properly installed |  |  |  |  |  |  | Condition of oil in sight glass? Clean Cloudy Dirty |  |  |
|  | Diesel Engine Condition Inspection |  |  |  |  |  |  | Visual lamp test |  |  |
|  | Fuel level is not less than 70% of full capacity |  |  |  |  |  |  | ANNUAL INSPECTION ITEMS |  |  |
|  | Controller selector switch is in “auto” position |  |  |  |  |  |  | Check pump shaft end play? |  |  |
|  | Batteries (2) voltage readings are normal |  |  |  |  |  |  | Check accuracy of pressure gauges and sensors? |  |  |
|  | Batteries (2) charging current is normal |  |  |  |  |  |  | Check pump coupling alignment? |  |  |
|  | Batteries (2) status indicator lamps are normal |  |  |  |  |  |  | Inspect emergency manual starting means (without power)? |  |  |
|  | Electrolyte level in batteries is normal |  |  |  |  |  |  | Tighten electrical connection as required? |  |  |
|  | Engine hour clock reading: |  |  | hours |  |  |  | Inspect mechanical moving parts for lubrication, excluding |  |  |
|  | Oil level in right angle gear drive is normal |  |  |  |  |  |  | starters/relays |  |  |
|  | Crankcase oil level is normal |  |  |  |  |  |  | Inspect calibrated pressure switch settings? |  |  |
|  | Condition of oil? Clean Cloudy Dirty |  |  |  |  |  |  | Inspect duct work for combustion air? |  |  |
|  | Cooling water level is normal |  |  |  |  |  |  | Inspect exhaust hangers and supports? |  |  |
|  | Water-jacket/engine block heater is operating |  |  |  |  |  |  |  |  |  |
| The information on this form (and in the documents attached here-to) attest to the fact that the equipment listed here-in was tested/inspected in conformance with applicable codes, bylaws, standards, and the manufacturer’s requirements by a qualified technician. The equipment was left in an operational condition except as noted in the spaces marked “comments”. This document has been provided to the building owner’s representative who has acknowledged receipt of same below. A copy should be maintained on the premises for examination by the Fire Marshal or Inspector at their request. |  |  |  |  |  |  |  |  |  |  |
| Company Name |  |  |  |  |  |  |  |  |  |  |
| Technician Performing Test |  |  | Certification Number/Stamp |  |  | Date |  |  | Technician Signature |  |

Building Fire Pump Tests (Continued)

| Date: |  |  |  |
| --- | --- | --- | --- |
| Building Name: |  | Address: |  |

“” = Yes - Tested correctly    “X” = No - Did not test correctly (NO answers are detailed in “Comments/Remarks”)     “NA” = Not applicable

| FIRE PUMP TESTING ITEMS |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| WEEKLY ACTION ITEMS |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Piping & Associated Equipment |  |  |  |  |  |  |  |  |  | Diesel Engine Driven Pump Test |  |  |  |  |  |  |  |
|  | Pump operated without flowing water: 10 minutes 30 minutes |  |  |  |  |  |  |  |  |  | Pump run for thirty (30) minutes |  |  |  |  |  |  |  |
|  | Packing gland checked. Minor leak at no flow? Yes No |  |  |  |  |  |  |  |  |  | Oil Pressure: |  |  |  | PSIG KPAG |  |  |  |
|  | Suction pressure at gauge: |  |  |  |  | PSIG KPAG |  |  |  |  | Oil Temperature: |  |  |  |  | C F |  |  |
|  | Discharge pressure at gauge : |  |  |  |  | PSIG KPAG |  |  |  |  | Engine Speed: |  |  |  |  | RPM |  |  |
|  | Packing gland adjusted as required? Yes No |  |  |  |  |  |  |  |  |  | Water Temperature: |  |  |  |  | C F |  |  |
|  | Checked for unusual noise or vibration? |  |  |  |  |  |  |  |  |  | Record time for diesel engine to crank: |  |  |  |  |  | seconds |  |
|  | Check packing boxes, bearings or pump casing for overheating? |  |  |  |  |  |  |  |  |  | Time for engine to normal run speed: |  |  |  |  |  | seconds |  |
|  | Record pump start pressure : |  |  |  |  | PSIG KPAG |  |  |  |  | Heat exchanger checked for cooling water flow? |  |  |  |  |  |  |  |
|  | Electrically Driven Pump Test |  |  |  |  |  |  |  |  |  | Is the controller performing run tests automatically? Yes No |  |  |  |  |  |  |  |
|  | Pump run for ten (10) minutes |  |  |  |  |  |  |  |  |  | Test log reviewed via visual display at controller? Yes No |  |  |  |  |  |  |  |
|  | Time for motor to accelerate to full speed: |  |  |  |  |  | seconds |  |  |  | Date last automatic test logged? |  |  |  |  |  |  |  |
|  | For reduced voltage or reduced current starting, record time |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | controller is on first step: |  |  |  |  | seconds |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Record automatic stop time: |  |  |  |  | minutes |  |  |  |  |  |  |  |  |  |  |  |  |
| FIRE PUMP TESTING |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Monthly testing |  |  |  |  |  |  |  |  |  | Semiannual |  |  |  |  |  |  |  |
|  | Exercise isolating switch & circuit breaker for proper operation? |  |  |  |  |  |  |  |  |  | Operate manual starting means (electrical) |  |  |  |  |  |  |  |
|  | Test circuit breakers and fuses for proper operation? |  |  |  |  |  |  |  |  |  | Operation of safety devices and alarms? |  |  |  |  |  |  |  |
|  | Test batteries for specific gravity and state of charge? |  |  |  |  |  |  |  |  |  | Check concentration of antifreeze? |  |  |  |  |  |  |  |
|  | Steam Systems Testing Procedure |  |  |  |  |  |  |  |  |  | Annual |  |  |  |  |  |  |  |
|  | Steam pressure gauge reading |  |  |  |  | PSIG KPAG |  |  |  |  | Operate emergency starting means (without power) |  |  |  |  |  |  |  |
|  | Time for turbine to reach operating speed: |  |  |  |  |  |  | seconds |  |  | Trip circuit breaker if provided? |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  | Diesel tanks and overflow piping unobstructed? |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  | Test exhaust for excessive back pressure? |  |  |  |  |  |  |  |
| Comments/Notations: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |