CAN/ULC-S537-04 – FIRE ALARM SYSTEM VERIFICATION REPORT
	Date:  
	
	

	Building Name:
	
	Address:
	



	
	CAN/ULC S537-04 (AMENDED FOR CAN/ULC-S524-06)
APPENDIX “C” ( INFORMATIVE) – FIRE ALARM SYSTEM (FAS)

VERIFICATION REPORTS
(Reference: Subsection 4.1-Note, Clause 4.2.1, 4.2.2)

C1.  FIRE ALARM SYSTEM VERIFICATION REPORT

 (Reference:  Clause 4.1.6, 4.1.7, 4.2.2)
	

	

	
	Electrical Permit Number:
	
	-
	
	
	Date:
	
	

	
	Building Name & Address:
	
	

	
	
	
	

	
	
	New FAS    FORMCHECKBOX 
      
	Existing FAS    FORMCHECKBOX 
   (See Note 1)
	

	
	System Manufacturer:
	
	Model Number:
	
	

	
	
	

	
	
	

	A
	System provides single-stage operation.
	Yes    FORMCHECKBOX 
        No   FORMCHECKBOX 

	

	B
	System provides two-stage operation.
	Yes    FORMCHECKBOX 
        No   FORMCHECKBOX 

	

	C
	The entire fire alarm system has been verified in accordance with CAN/ULC-S537-04, Standard for Verification of Fire Alarm Systems.
	Yes    FORMCHECKBOX 
        No   FORMCHECKBOX 
      
	

	D
	This is a partial verification for a partial occupancy.
	Yes    FORMCHECKBOX 
        No   FORMCHECKBOX 
      
	

	E
	Components of the existing Fire Alarm System have been modified or replaced with components from a different manufacturer and are compatible with the existing Fire Alarm System components. (See Note 2)
	Yes    FORMCHECKBOX 
        No   FORMCHECKBOX 
      
	

	F
	This is a partial verification for a Fire Alarm System that has been replaced in stages.
	Yes    FORMCHECKBOX 
        No   FORMCHECKBOX 
      
	

	G
	This is a verification of a portion of an existing Fire Alarm System verified in accordance with Section 6, System Modifications.
	Yes    FORMCHECKBOX 
        No   FORMCHECKBOX 
      
	

	H
	Installed in accordance with the design and CAN/ULC-S524, Standard for the Installation of Fire Alarm Systems.
	Yes    FORMCHECKBOX 
        No   FORMCHECKBOX 
      
	

	I
	The Fire Alarm System documentation is on site and includes a description of the system.
	Yes    FORMCHECKBOX 
        No   FORMCHECKBOX 
      
	

	J
	The Fire Alarm System is now fully functional with   FORMCHECKBOX 
    without  FORMCHECKBOX 
  deficiencies. (See Note 3)
	Yes    FORMCHECKBOX 
        No   FORMCHECKBOX 
      N/A    FORMCHECKBOX 

	

	K
	The Fire Alarm System is connected to an acceptable ULC Listed central monitoring station.
	Yes    FORMCHECKBOX 
        No   FORMCHECKBOX 
      
	

	
	The communicator is ULC Listed for the purpose.
	Yes    FORMCHECKBOX 
        No   FORMCHECKBOX 
      
	

	
	The connections between the FAS and the communicator are supervised.
	Yes    FORMCHECKBOX 
        No   FORMCHECKBOX 
      
	

	
	If connected, the name and location of the central monitoring station is:
	
	

	
	
	
	

	
	ULC “Central Station Fire Protective Signalling Service” Certificate Number:
	
	
	

	
	which is issued for the above noted central monitoring station address is  FORMCHECKBOX 
   is not  FORMCHECKBOX 
  attached.
	
	

	L
	Comments:
	

	
	
	

	
	
	

	M
	A copy of this report will be given to:
	
	Yes    FORMCHECKBOX 
        No   FORMCHECKBOX 

	

	
	who is the owner or owner’s representative for this building.
	
	

	CERTIFICATION

	This certifies that the information contained in this Fire Alarm System Verification Report  (which incorporates the attached
	
	pages)

	is correct and complete.   The system and equipment described here-in was tested/inspected in conformance with CAN/ULC-S537-04 by a qualified technician.  The equipment was left in an operational condition except as noted above.  A copy of this report must be maintained on the premises for examination by the Fire Marshal, Building Inspector, or other Authority Having Jurisdiction at their request.

	

	
	Supervising Technician:
	Company & Contact Information:
	
	(Stamp Field)
	

	
	
	
	
	
	

	
	
	
	
	
	

	
	Print Name:
	
	
	
	
	

	
	
	Telephone:
	
	
	
	

	
	Assisting Technician/Electrician:
	Company & Contact Information:
	
	
	

	
	
	
	
	
	

	
	
	
	
	
	

	
	Print Name:
	
	
	
	
	

	
	
	Telephone:
	
	
	
	

	
	Designer:
	Company & Contact Information:
	
	
	

	
	
	
	
	
	

	
	
	
	
	
	

	
	Print Name:
	
	
	
	
	

	
	
	Telephone:
	
	
	
	

	

	NOTES:
	

	1.
	Extent of Verification of the existing FAS:
	

	
	

	
	

	2.
	If “Yes”, ULC test report/compatibility listing is attached.

	3.
	The identified deficiencies relate to:

	
	 FORMCHECKBOX 

	(a) the existing portion of the FAS not covered by the scope of work under the above referenced permit.

	
	 FORMCHECKBOX 

	(b) the newly installed FAS (or modified/added portion of FAS) under the above referenced permit.


 “Yes” - Tested correctly    “No” - Did not test correctly (NO answers are typically detailed in “Comments/Remarks”)

 “NA” = Not applicable
	C2. Documentation

	
	Yes
	No
	N/A

	A
	Instructions for resetting the system and silencing alarm signals.
	
	 FORMCHECKBOX 

	 FORMCHECKBOX 

	 FORMCHECKBOX 


	B
	Instructions for silencing the trouble signal and action to be taken when the trouble signal sounds.
	
	 FORMCHECKBOX 

	 FORMCHECKBOX 

	 FORMCHECKBOX 


	C
	Description of the function of each operating control and indicator on the fire alarm control unit.
	
	 FORMCHECKBOX 

	 FORMCHECKBOX 

	 FORMCHECKBOX 


	D
	Description of the area or fire zone protected by each alarm detection circuit (this may be in the form of a list or plan drawing).
	
	 FORMCHECKBOX 

	 FORMCHECKBOX 

	 FORMCHECKBOX 


	E
	Description of alarm signal operation.
	
	 FORMCHECKBOX 

	 FORMCHECKBOX 

	 FORMCHECKBOX 


	F
	Description of ancillary equipment controlled by the fire alarm system.
	
	 FORMCHECKBOX 

	 FORMCHECKBOX 

	 FORMCHECKBOX 


	G
	In systems that provide logical control of a smoke control system, documentation is on site and includes a sequence of operation of the smoke control system.
	
	 FORMCHECKBOX 

	 FORMCHECKBOX 

	 FORMCHECKBOX 


	
	Smoke control installed in accordance with Measure:
	
	
	
	
	
	

	H
	Building diagrams are on site that clearly indicate the type and location of all smoke control equipment (fans, dampers, etc.).
	
	 FORMCHECKBOX 

	 FORMCHECKBOX 

	 FORMCHECKBOX 


	Recommended Additional Documentation (not mandated by the Standard):
	Yes
	No
	

	
	Additional documentation relating to smoke control measures in the building is appended to this report.
	
	 FORMCHECKBOX 

	 FORMCHECKBOX 

	

	
	Fire Safety Plan documentation is on site.
	
	 FORMCHECKBOX 

	 FORMCHECKBOX 

	

	
	Instructions to Occupants/Evacuation Floor Plans are posted.
	
	 FORMCHECKBOX 

	 FORMCHECKBOX 

	

	
	There are a total of:
	
	remotely installed amplifiers in this FAS.

	
	
	
	supervised power supplies in this FAS.

	
	
	
	remote sequential display units in this FAS.

	
	
	
	remote annunciators in this FAS.

	
	
	
	remote trouble units in this FAS.

	
	
	
	stand-by batteries in this FAS.

	
	
	
	remote booster/power supplies in this FAS.

	List all locations where remote booster/power  supplies, batteries & amplifiers are installed:

	

	

	


	C3. Field Device and Related Circuits – Test and Inspection

	
	Yes
	No
	N/A

	A
	Correct field termination and wiring size.
	
	 FORMCHECKBOX 

	 FORMCHECKBOX 

	 FORMCHECKBOX 


	B
	Correct circuit polarities.
	
	 FORMCHECKBOX 

	 FORMCHECKBOX 

	 FORMCHECKBOX 


	C
	An open circuit fault on a conventional device circuit causes a trouble signal.
	
	 FORMCHECKBOX 

	 FORMCHECKBOX 

	 FORMCHECKBOX 


	D
	Removal of any active or supporting field device circuit causes a trouble signal.
	
	 FORMCHECKBOX 

	 FORMCHECKBOX 

	 FORMCHECKBOX 


	E
	One contact device and one non-contact device tested for operation and annunciation at the control unit or transponder, when using a field verifying device.
	
	 FORMCHECKBOX 

	 FORMCHECKBOX 

	 FORMCHECKBOX 


	F
	Class “A” circuits serving conventional field devices tested for the capability of providing an alarm signal on each side of an open circuit fault connection at the electrically most remote point in the circuit.
	
	 FORMCHECKBOX 

	 FORMCHECKBOX 

	 FORMCHECKBOX 


	G
	Ground fault indications occur when tested at the electrically furthest field device, and do not result in normal to off-normal status change conditions.
	
	 FORMCHECKBOX 

	 FORMCHECKBOX 

	 FORMCHECKBOX 


	H
	Field device at the electrically furthest point from the power source (in every circuit) receives rated power in accordance with the manufacturer’s specifications.
	
	 FORMCHECKBOX 

	 FORMCHECKBOX 

	 FORMCHECKBOX 


	I
	Replaceable over-current devices are of the correct rating.
	
	 FORMCHECKBOX 

	 FORMCHECKBOX 

	 FORMCHECKBOX 


	J
	Where a power buss circuit serves more than one fire alarm zone, a single fault (open circuit fault, short circuit fault or ground fault) on the power circuit does not prevent the normal operation of input or output field devices in more than one fire alarm zone.
	
	 FORMCHECKBOX 

	 FORMCHECKBOX 

	 FORMCHECKBOX 


	K
	Conductor type and wire gauge are in accordance with the equipment manufacturer’s installation wiring requirements at all system termination points.
	
	 FORMCHECKBOX 

	 FORMCHECKBOX 

	 FORMCHECKBOX 


	L
	Confirm that where multiple strand optical fibre cable used with a fire alarm system is not dedicated to the fire alarm system, the fire alarm system shall continue to function as required despite impairment to other systems which may share the cable.
	
	 FORMCHECKBOX 

	 FORMCHECKBOX 

	 FORMCHECKBOX 



	C4. Data Communication Link Testing

	Control Unit/Transponder Field Location:
	
	

	Control Unit/Transponder Identification:
	
	

	DCL Identification:
	
	

	
	Yes
	No
	N/A

	A
	Each system abnormal condition specified in Table 1 – Abnormal System Conditions, tested for each data communication link at the control unit or transponder.
	
	 FORMCHECKBOX 

	 FORMCHECKBOX 

	 FORMCHECKBOX 


	B
	Tests for alarm and trouble received under a single ground fault condition conducted on each conductor of that data communication link independently.
	
	 FORMCHECKBOX 

	 FORMCHECKBOX 

	 FORMCHECKBOX 


	C
	Each conductor in a data communication link, Class A (DCLA) tested for the capability of providing an alarm signal on each side of a single open circuit fault condition.
	
	 FORMCHECKBOX 

	 FORMCHECKBOX 

	 FORMCHECKBOX 


	D
	Where a data communication link serves devices on more than one floor area, impose a wire-to-wire short circuit fault within each floor area and confirm receipt of trouble and alarm condition from another floor area.
	
	 FORMCHECKBOX 

	 FORMCHECKBOX 

	 FORMCHECKBOX 


	E
	Where fault isolation modules are installed in data communication links serving field devices, wiring shorted on the isolated side, annunciation of the fault confirmed, and then a device on the source side operated, and activation confirmed at the control unit or transponder.
	
	 FORMCHECKBOX 

	 FORMCHECKBOX 

	 FORMCHECKBOX 


	F
	Where fault isolation in data communication links is provided between control units or transponders, the field wiring shorted between each pair of control units or transponders, in turn, annunciation of the fault confirmed and operation outside the shorted section is confirmed.
	
	 FORMCHECKBOX 

	 FORMCHECKBOX 

	 FORMCHECKBOX 


	

	Control Unit/Transponder Field Location:
	
	

	Control Unit/Transponder Identification:
	
	

	DCL Identification:
	
	

	
	Yes
	No
	N/A

	A
	Each system abnormal condition specified in Table 1 – Abnormal System Conditions, tested for each data communication link at the control unit or transponder.
	
	 FORMCHECKBOX 

	 FORMCHECKBOX 

	 FORMCHECKBOX 


	B
	Tests for alarm and trouble received under a single ground fault condition conducted on each conductor of that data communication link independently.
	
	 FORMCHECKBOX 

	 FORMCHECKBOX 

	 FORMCHECKBOX 


	C
	Each conductor in a data communication link, Class A (DCLA) tested for the capability of providing an alarm signal on each side of a single open circuit fault condition.
	
	 FORMCHECKBOX 

	 FORMCHECKBOX 

	 FORMCHECKBOX 


	D
	Where a data communication link serves devices on more than one floor area, impose a wire-to-wire short circuit fault within each floor area and confirm receipt of trouble and alarm condition from another floor area.
	
	 FORMCHECKBOX 

	 FORMCHECKBOX 

	 FORMCHECKBOX 


	E
	Where fault isolation modules are installed in data communication links serving field devices, wiring shorted on the isolated side, annunciation of the fault confirmed, and then a device on the source side operated, and activation confirmed at the control unit or transponder.
	
	 FORMCHECKBOX 

	 FORMCHECKBOX 

	 FORMCHECKBOX 


	F
	Where fault isolation in data communication links is provided between control units or transponders, the field wiring shorted between each pair of control units or transponders, in turn, annunciation of the fault confirmed and operation outside the shorted section is confirmed.
	
	 FORMCHECKBOX 

	 FORMCHECKBOX 

	 FORMCHECKBOX 



	C5.1 Control Unit or Transponder Tests
(Reference Clause 5.1.1)

	Control Unit/Transponder Field Location:
	
	

	Control Unit/Transponder Identification:
	
	

	
	Yes
	No
	N/A

	A
	Power ‘on’ visual indicator operates.
	
	 FORMCHECKBOX 

	 FORMCHECKBOX 

	 FORMCHECKBOX 


	B
	Common visual trouble signal operates.
	
	 FORMCHECKBOX 

	 FORMCHECKBOX 

	 FORMCHECKBOX 


	C
	Common audible trouble signal operates.
	
	 FORMCHECKBOX 

	 FORMCHECKBOX 

	 FORMCHECKBOX 


	D
	Trouble signal silence switch operates.
	
	 FORMCHECKBOX 

	 FORMCHECKBOX 

	 FORMCHECKBOX 


	E
	Main Power supply failure trouble signal operates.
	
	 FORMCHECKBOX 

	 FORMCHECKBOX 

	 FORMCHECKBOX 


	F
	Ground fault tested on positive and negative initiates trouble signal.
	
	 FORMCHECKBOX 

	 FORMCHECKBOX 

	 FORMCHECKBOX 


	G
	Alert signal operates.
	
	 FORMCHECKBOX 

	 FORMCHECKBOX 

	 FORMCHECKBOX 


	H
	Alarm signal operates. 
	
	 FORMCHECKBOX 

	 FORMCHECKBOX 

	 FORMCHECKBOX 


	I
	Automatic transfer from alert signal to alarm signal operates.
	Time:
	
	
	 FORMCHECKBOX 

	 FORMCHECKBOX 

	 FORMCHECKBOX 


	J
	Manual transfer from alert signal to alarm signal.
	
	 FORMCHECKBOX 

	 FORMCHECKBOX 

	 FORMCHECKBOX 


	K
	Automatic transfer from alert to alarm signal cancel (acknowledge) operates on a two stage system.
	
	 FORMCHECKBOX 

	 FORMCHECKBOX 

	 FORMCHECKBOX 


	L
	Alarm signal silence inhibit function operates.
	
	 FORMCHECKBOX 

	 FORMCHECKBOX 

	 FORMCHECKBOX 


	M
	Alarm signal manual silence operates.
	
	 FORMCHECKBOX 

	 FORMCHECKBOX 

	 FORMCHECKBOX 


	N
	Alarm signal silence visual indication operates
	
	 FORMCHECKBOX 

	 FORMCHECKBOX 

	 FORMCHECKBOX 


	O
	Alarm signal and visible signal devices, when silenced, automatically reinitiate upon subsequent alarm.
                 FORMCHECKBOX 
 In same zone           FORMCHECKBOX 
 In other zone/circuit
	
	 FORMCHECKBOX 

	 FORMCHECKBOX 

	 FORMCHECKBOX 


	P
	Alarm signal silence automatic cut-out timer.
	Time:
	
	
	 FORMCHECKBOX 

	 FORMCHECKBOX 

	 FORMCHECKBOX 


	Q
	Audible, visual, alert, and alarm signals programmed and operate as per manufacturer’s design and specification.
	
	 FORMCHECKBOX 

	 FORMCHECKBOX 

	 FORMCHECKBOX 


	R
	Input circuit alarm and supervisory operation including audible and visual indicator operates.
	
	 FORMCHECKBOX 

	 FORMCHECKBOX 

	 FORMCHECKBOX 


	S
	Input circuit supervision fault causes a trouble indication.
	
	 FORMCHECKBOX 

	 FORMCHECKBOX 

	 FORMCHECKBOX 


	T
	Output circuit alarm indicators operate.
	
	 FORMCHECKBOX 

	 FORMCHECKBOX 

	 FORMCHECKBOX 


	U
	Output circuit supervision fault causes a trouble indication.
	
	 FORMCHECKBOX 

	 FORMCHECKBOX 

	 FORMCHECKBOX 


	V
	Visual indicator test (lamp test) operates.
	
	 FORMCHECKBOX 

	 FORMCHECKBOX 

	 FORMCHECKBOX 


	W
	Coded signal sequence operate not less than the required number of times and the correct alarm signal thereafter.
	
	 FORMCHECKBOX 

	 FORMCHECKBOX 

	 FORMCHECKBOX 


	X
	Coded signal sequences are not interrupted by subsequent alarms.
	
	 FORMCHECKBOX 

	 FORMCHECKBOX 

	 FORMCHECKBOX 


	Y
	Ancillary device control circuit is rated for the intended purpose.
	
	 FORMCHECKBOX 

	 FORMCHECKBOX 

	 FORMCHECKBOX 


	Z
	Ancillary device by-pass results in trouble signal.
	
	 FORMCHECKBOX 

	 FORMCHECKBOX 

	 FORMCHECKBOX 


	AA
	Input circuit to output circuit operation including ancillary device circuits (refer to Appendix C5.12, Ancillary Device Circuit Test), for correct program operation as per design and specification.
	
	 FORMCHECKBOX 

	 FORMCHECKBOX 

	 FORMCHECKBOX 


	BB
	Fire alarm reset function operates.
	
	 FORMCHECKBOX 

	 FORMCHECKBOX 

	 FORMCHECKBOX 


	CC
	Main power to emergency power supply transfer operates.
	
	 FORMCHECKBOX 

	 FORMCHECKBOX 

	 FORMCHECKBOX 


	DD
	Control unit or transponder enclosure bonded to ground.
	
	 FORMCHECKBOX 

	 FORMCHECKBOX 

	 FORMCHECKBOX 


	EE
	Status change confirmation feature (smoke detectors only) verified.
	
	 FORMCHECKBOX 

	 FORMCHECKBOX 

	 FORMCHECKBOX 


	Recommended Additional Testing (not mandated by the Standard):
	
	Yes
	No
	N/A

	Alarm, trouble, & supervisory relays function correctly.
	
	 FORMCHECKBOX 

	 FORMCHECKBOX 

	 FORMCHECKBOX 


	Is an AC disconnecting switch installed?                         YES   FORMCHECKBOX 
       NO   FORMCHECKBOX 

(ULC CAN4-S524 restricts this, but some AHJ’s will accept it.  
A “YES” answer here must be noted in the “Comments/Remarks” section of this report.)


	C5.2 Voice Communication Test

	Location:
	
	

	Identification:
	
	

	
	Yes
	No
	N/A

	A
	Power ‘on’ visual indicator operates.
	
	 FORMCHECKBOX 

	 FORMCHECKBOX 

	 FORMCHECKBOX 


	B
	Common visual trouble signal operates.
	
	 FORMCHECKBOX 

	 FORMCHECKBOX 

	 FORMCHECKBOX 


	C
	Common audible trouble signal operates.
	
	 FORMCHECKBOX 

	 FORMCHECKBOX 

	 FORMCHECKBOX 


	D
	Trouble signal silence switch operates.
	
	 FORMCHECKBOX 

	 FORMCHECKBOX 

	 FORMCHECKBOX 


	E
	All-call voice paging, including visual indicator, operates.
	
	 FORMCHECKBOX 

	 FORMCHECKBOX 

	 FORMCHECKBOX 


	F
	Output circuits for selective voice paging, including visual indication, operates.
	
	 FORMCHECKBOX 

	 FORMCHECKBOX 

	 FORMCHECKBOX 


	G
	Output circuits for selective voice paging trouble operation, including visual indication, operates.
	
	 FORMCHECKBOX 

	 FORMCHECKBOX 

	 FORMCHECKBOX 


	H
	Microphone, including press to talk switch, operates. 
	
	 FORMCHECKBOX 

	 FORMCHECKBOX 

	 FORMCHECKBOX 


	I
	Operation of voice paging does not interfere with initial inhibit time of alert signal and alarm signal.
	
	 FORMCHECKBOX 

	 FORMCHECKBOX 

	 FORMCHECKBOX 


	J
	All-call voice paging operates (on emergency power supply).
	
	 FORMCHECKBOX 

	 FORMCHECKBOX 

	 FORMCHECKBOX 


	K
	Upon failure of one amplifier, system automatically transfers to backup amplifier(s).
	
	 FORMCHECKBOX 

	 FORMCHECKBOX 

	 FORMCHECKBOX 


	L
	Circuits for emergency telephone call-in operation, including audible and visual indication operates.
	
	 FORMCHECKBOX 

	 FORMCHECKBOX 

	 FORMCHECKBOX 


	M
	Circuits for emergency telephones for operation, including two-way voice communication, operates.
	
	 FORMCHECKBOX 

	 FORMCHECKBOX 

	 FORMCHECKBOX 


	N
	Circuits for emergency telephone trouble operation, including visual indication, operates.
	
	 FORMCHECKBOX 

	 FORMCHECKBOX 

	 FORMCHECKBOX 


	O
	Emergency telephone verbal communication operates.
	
	 FORMCHECKBOX 

	 FORMCHECKBOX 

	 FORMCHECKBOX 


	P
	Emergency telephone operable or in-use tone at handset operates.
	
	 FORMCHECKBOX 

	 FORMCHECKBOX 

	 FORMCHECKBOX 


	Q
	While in standby mode, voice communication busses used for paging, alert signal, alarm signal, and emergency telephone communication circuits, an open circuit fault, or short circuit fault, or operation of an overcurrent protective device provided for the purpose, shall result in a specific trouble indication specific to the faulty buss.
	
	 FORMCHECKBOX 

	 FORMCHECKBOX 

	 FORMCHECKBOX 


	Recommended Additional Testing (not mandated by the Standard):
	Yes
	No
	N/A

	Visual indicator test (lamp test) operates.
	
	 FORMCHECKBOX 

	 FORMCHECKBOX 

	 FORMCHECKBOX 


	Main power to emergency power supply transfer operates.
	
	 FORMCHECKBOX 

	 FORMCHECKBOX 

	 FORMCHECKBOX 


	Communication control enclosure bonded to ground.
	
	 FORMCHECKBOX 

	 FORMCHECKBOX 

	 FORMCHECKBOX 


	Trouble signal on the voice communication system results in common trouble signal on the fire alarm system.
	
	 FORMCHECKBOX 

	 FORMCHECKBOX 

	 FORMCHECKBOX 


	Dead-front panel(s) in place & as per manufacturer’s specification.
	
	 FORMCHECKBOX 

	 FORMCHECKBOX 

	 FORMCHECKBOX 



	C5.3 Required System Response Times

	Control Unit/Transponder Field Location:
	
	

	Control Unit/Transponder Identification:
	
	

	
	Yes
	No
	N/A

	A
	Audible signal devices and visible signal devices operated within ten seconds and; 
	
	 FORMCHECKBOX 

	 FORMCHECKBOX 

	

	
	subsequent input operated within ten seconds.
	
	 FORMCHECKBOX 

	 FORMCHECKBOX 

	

	B
	Remote connection operated within ten seconds.
	
	 FORMCHECKBOX 

	 FORMCHECKBOX 

	 FORMCHECKBOX 


	C
	Release device start of sequence operated within ten seconds.
	
	 FORMCHECKBOX 

	 FORMCHECKBOX 

	 FORMCHECKBOX 


	D
	Required Annunciation operated within ten seconds
and; 
	
	 FORMCHECKBOX 

	 FORMCHECKBOX 

	

	
	subsequent input operation within ten seconds.
	
	 FORMCHECKBOX 

	 FORMCHECKBOX 

	

	E
	Required central alarm and control facility operated within ten seconds and; 
	
	 FORMCHECKBOX 

	 FORMCHECKBOX 

	 FORMCHECKBOX 


	
	subsequent input operation within ten seconds.
	
	 FORMCHECKBOX 

	 FORMCHECKBOX 

	 FORMCHECKBOX 


	F
	Ancillary circuits operated within ten seconds.
	
	 FORMCHECKBOX 

	 FORMCHECKBOX 

	 FORMCHECKBOX 


	

	Control Unit/Transponder Field Location:
	
	

	Control Unit/Transponder Identification:
	
	

	
	Yes
	No
	N/A

	A
	Audible signal devices and visible signal devices operated within ten seconds and; 
	
	 FORMCHECKBOX 

	 FORMCHECKBOX 

	

	
	subsequent input operated within ten seconds.
	
	 FORMCHECKBOX 

	 FORMCHECKBOX 

	

	B
	Remote connection operated within ten seconds.
	
	 FORMCHECKBOX 

	 FORMCHECKBOX 

	 FORMCHECKBOX 


	C
	Release device start of sequence operated within ten seconds.
	
	 FORMCHECKBOX 

	 FORMCHECKBOX 

	 FORMCHECKBOX 


	D
	Required Annunciation operated within ten seconds

and; 
	
	 FORMCHECKBOX 

	 FORMCHECKBOX 

	

	
	subsequent input operation within ten seconds.
	
	 FORMCHECKBOX 

	 FORMCHECKBOX 

	

	E
	Required central alarm and control facility operated within ten seconds and; 
	
	 FORMCHECKBOX 

	 FORMCHECKBOX 

	 FORMCHECKBOX 


	
	subsequent input operation within ten seconds.
	
	 FORMCHECKBOX 

	 FORMCHECKBOX 

	 FORMCHECKBOX 


	F
	Ancillary circuits operated within ten seconds.
	
	 FORMCHECKBOX 

	 FORMCHECKBOX 

	 FORMCHECKBOX 


	

	Control Unit/Transponder Field Location:
	
	

	Control Unit/Transponder Identification:
	
	

	
	Yes
	No
	N/A

	A
	Audible signal devices and visible signal devices operated within ten seconds and; 
	
	 FORMCHECKBOX 

	 FORMCHECKBOX 

	

	
	subsequent input operated within ten seconds.
	
	 FORMCHECKBOX 

	 FORMCHECKBOX 

	

	B
	Remote connection operated within ten seconds.
	
	 FORMCHECKBOX 

	 FORMCHECKBOX 

	 FORMCHECKBOX 


	C
	Release device start of sequence operated within ten seconds.
	
	 FORMCHECKBOX 

	 FORMCHECKBOX 

	 FORMCHECKBOX 


	D
	Required Annunciation operated within ten seconds

and; 
	
	 FORMCHECKBOX 

	 FORMCHECKBOX 

	

	
	subsequent input operation within ten seconds.
	
	 FORMCHECKBOX 

	 FORMCHECKBOX 

	

	E
	Required central alarm and control facility operated within ten seconds and; 
	
	 FORMCHECKBOX 

	 FORMCHECKBOX 

	 FORMCHECKBOX 


	
	subsequent input operation within ten seconds.
	
	 FORMCHECKBOX 

	 FORMCHECKBOX 

	 FORMCHECKBOX 


	F
	Ancillary circuits operated within ten seconds.
	
	 FORMCHECKBOX 

	 FORMCHECKBOX 

	 FORMCHECKBOX 


	

	Control Unit/Transponder Field Location:
	
	

	Control Unit/Transponder Identification:
	
	

	
	Yes
	No
	N/A

	A
	Audible signal devices and visible signal devices operated within ten seconds and; 
	
	 FORMCHECKBOX 

	 FORMCHECKBOX 

	

	
	subsequent input operated within ten seconds.
	
	 FORMCHECKBOX 

	 FORMCHECKBOX 

	

	B
	Remote connection operated within ten seconds.
	
	 FORMCHECKBOX 

	 FORMCHECKBOX 

	 FORMCHECKBOX 


	C
	Release device start of sequence operated within ten seconds.
	
	 FORMCHECKBOX 

	 FORMCHECKBOX 

	 FORMCHECKBOX 


	D
	Required Annunciation operated within ten seconds

and; 
	
	 FORMCHECKBOX 

	 FORMCHECKBOX 

	

	
	subsequent input operation within ten seconds.
	
	 FORMCHECKBOX 

	 FORMCHECKBOX 

	

	E
	Required central alarm and control facility operated within ten seconds and; 
	
	 FORMCHECKBOX 

	 FORMCHECKBOX 

	 FORMCHECKBOX 


	
	subsequent input operation within ten seconds.
	
	 FORMCHECKBOX 

	 FORMCHECKBOX 

	 FORMCHECKBOX 


	F
	Ancillary circuits operated within ten seconds.
	
	 FORMCHECKBOX 

	 FORMCHECKBOX 

	 FORMCHECKBOX 



	C5.4 Control Unit or Transponder Inspection

	Control Unit/Transponder Field Location:
	
	

	Control Unit/Transponder Identification:
	
	

	
	Yes
	No
	N/A

	A
	Input circuit designations correctly identified in relation to connected field devices.
	
	 FORMCHECKBOX 

	 FORMCHECKBOX 

	 FORMCHECKBOX 


	B
	Output circuit designations correctly identified in relation to connected field devices.
	
	 FORMCHECKBOX 

	 FORMCHECKBOX 

	 FORMCHECKBOX 


	C
	Correct designations for common control functions and indicators.
	
	 FORMCHECKBOX 

	 FORMCHECKBOX 

	 FORMCHECKBOX 


	D
	Plug-in components and modules securely in place.
	
	 FORMCHECKBOX 

	 FORMCHECKBOX 

	 FORMCHECKBOX 


	E
	Plug-in cables securely in place.
	
	 FORMCHECKBOX 

	 FORMCHECKBOX 

	 FORMCHECKBOX 


	F
	Record the date, revision and version of firmware:
	
	
	
	

	
	Date:
	
	Revision:
	
	Version:
	
	
	
	

	
	Record the date, revision and version of the program software:
	
	
	
	

	
	Date:
	
	Revision:
	
	Version:
	
	
	
	

	G
	Control unit/transponder is clean and free of dust and dirt.
	
	 FORMCHECKBOX 

	 FORMCHECKBOX 

	 FORMCHECKBOX 


	H
	Fuses in accordance with the manufacturer’s specification.
	
	 FORMCHECKBOX 

	 FORMCHECKBOX 

	 FORMCHECKBOX 


	I
	Control unit/transponder lock is functional.
	
	 FORMCHECKBOX 

	 FORMCHECKBOX 

	 FORMCHECKBOX 


	J
	Termination points for wiring to field devices secure.
	
	 FORMCHECKBOX 

	 FORMCHECKBOX 

	 FORMCHECKBOX 


	K
	Control unit/transponder power disconnects in accordance with C22.1, Safety Standard for Electrical Installations, Canadian Electrical Code, 

Part 1.
	
	 FORMCHECKBOX 

	 FORMCHECKBOX 

	 FORMCHECKBOX 


	L
	Field wiring entry points for the various circuits and circuit separations are in accordance with the manufacturer’s installation instructions.
	
	 FORMCHECKBOX 

	 FORMCHECKBOX 

	 FORMCHECKBOX 


	M
	Main power supply feed wiring is in accordance with the manufacturer’s specifications.
	
	 FORMCHECKBOX 

	 FORMCHECKBOX 

	 FORMCHECKBOX 


	N
	Verify control units/transponders with stand-alone capability serve the same area for both input circuits and output circuits.
	
	 FORMCHECKBOX 

	 FORMCHECKBOX 

	 FORMCHECKBOX 


	O
	Control units or transponders which operate with stand-alone capability have signal silence, reset, and trouble silence switches with visual indications, degraded mode capability and stand-alone capability indicators.
	
	 FORMCHECKBOX 

	 FORMCHECKBOX 

	 FORMCHECKBOX 


	P
	Each control unit/transponder has been furnished with installation, operating and maintenance instructions.
	
	 FORMCHECKBOX 

	 FORMCHECKBOX 

	 FORMCHECKBOX 


	Q
	Control unit/transponder visual indicators comply with Table 3 – Visual Indicators Colour Code.
	
	 FORMCHECKBOX 

	 FORMCHECKBOX 

	 FORMCHECKBOX 


	Recommended Additional Visual Inspection (not mandated by the Standard):
	
	Yes
	No
	N/A

	Dead-front panel(s) in place & as per manufacturer’s specification.
	
	 FORMCHECKBOX 

	 FORMCHECKBOX 

	 FORMCHECKBOX 



	C5.5 Large Scale Network Systems

	Control Unit/Transponder Field Location:
	
	

	Control Unit/Transponder Identification:
	
	

	
	Yes
	No
	N/A

	A
	Verify control units/transponders serve the same area for both input circuits and output circuits.
	
	
	
	

	B
	Verify control units/transponders with stand-alone capability have signal silence, reset, and trouble silence switches with visual indicators, degraded mode capability and stand-alone capability indicators.
	
	
	
	

	C
	Confirm that between any nodes a single open circuit fault, wire-to-wire short circuit fault, or ground fault on the network results in a trouble signal at each node and continued alarm receipt capability at each node under these conditions.
	
	
	
	

	D
	To test stand-alone capability, create a condition of data communication link failure, and confirm each control unit or transponder is capable of receiving an alarm initiation and provides output operation in the area as served by the control unit or transponder in degraded mode.
	
	
	
	

	E
	To test degraded mode capability, create a condition of data communication link failure in two separate locations creating two network segments, and confirm each segment of the network has the following operation:
	
	
	
	

	
	(i)
	Operate the alarm signals in accordance with the system operating sequence;
	
	
	
	

	
	(ii)
	Maintain synchronization of control units or transponders for alert signals and alarm signals;
	
	
	
	

	
	(iii)
	Operate local relays in control units or transponders connected to ancillary devices as required;
	
	
	
	

	
	(iv)
	Confirm the operation of acknowledge, signal silence, reset and trouble silence switches with visual indicators, degraded mode capability and stand-alone capability indicators are functional for each network segment.
	
	
	
	

	C5.5 Large Scale Network Systems

	Control Unit/Transponder Field Location:
	
	

	Control Unit/Transponder Identification:
	
	

	
	Yes
	No
	N/A

	A
	Verify control units/transponders serve the same area for both input circuits and output circuits.
	
	
	
	

	B
	Verify control units/transponders with stand-alone capability have signal silence, reset, and trouble silence switches with visual indicators, degraded mode capability and stand-alone capability indicators.
	
	
	
	

	C
	Confirm that between any nodes a single open circuit fault, wire-to-wire short circuit fault, or ground fault on the network results in a trouble signal at each node and continued alarm receipt capability at each node under these conditions.
	
	
	
	

	D
	To test stand-alone capability, create a condition of data communication link failure, and confirm each control unit or transponder is capable of receiving an alarm initiation and provides output operation in the area as served by the control unit or transponder in degraded mode.
	
	
	
	

	E
	To test degraded mode capability, create a condition of data communication link failure in two separate locations creating two network segments, and confirm each segment of the network has the following operation:
	
	
	
	

	
	(i)
	Operate the alarm signals in accordance with the system operating sequence;
	
	
	
	

	
	(ii)
	Maintain synchronization of control units or transponders for alert signals and alarm signals;
	
	
	
	

	
	(iii)
	Operate local relays in control units or transponders connected to ancillary devices as required;
	
	
	
	

	
	(iv)
	Confirm the operation of acknowledge, signal silence, reset and trouble silence switches with visual indicators, degraded mode capability and stand-alone capability indicators are functional for each network segment.
	
	
	
	


	C5.6 Power Supply Inspection

	Power Supply Field Location:
	
	

	Power Supply Identification:
	
	

	Circuit Disconnect Means Location:
	
	

	Circuit Panel/Breaker Identification:
	
	

	
	Yes
	No
	N/A

	A
	Conforms with the requirements of CAN/ULC-S524, Standard for the Installation of Fire Alarm Systems; and C22.1, Safety Standard for Electrical Installations, Canadian Electrical Code, Part 1, Section 32.
	
	 FORMCHECKBOX 

	 FORMCHECKBOX 

	 FORMCHECKBOX 


	B
	Fused in accordance with the manufacturer’s marked rating of the system.
	
	 FORMCHECKBOX 

	 FORMCHECKBOX 

	 FORMCHECKBOX 


	C
	Equipped with the identified disconnect means.
	
	 FORMCHECKBOX 

	 FORMCHECKBOX 

	 FORMCHECKBOX 


	D
	Adequate to meet the requirements of the system.
	
	 FORMCHECKBOX 

	 FORMCHECKBOX 

	 FORMCHECKBOX 


	E
	Power for ancillary devices is taken from a source separate from the fire alarm system control unit or transponder power supply.
	
	 FORMCHECKBOX 

	 FORMCHECKBOX 

	 FORMCHECKBOX 


	F
	Power for ancillary devices is taken from the control unit or transponder that is designed to provide such power.
	
	 FORMCHECKBOX 

	 FORMCHECKBOX 

	 FORMCHECKBOX 


	G
	Ancillary devices, which are powered from the control unit or transponder, are recorded.
	
	 FORMCHECKBOX 

	 FORMCHECKBOX 

	 FORMCHECKBOX 


	H
	Where fault isolation in power distribution riser has been provided, tests have been conducted to ensure a wire-to-wire short in the field wiring between each pair of control units or transponders, in turn, results in annunciation of the fault and continued operation outside of the shorted section confirmed. 
	
	 FORMCHECKBOX 

	 FORMCHECKBOX 

	 FORMCHECKBOX 


	Recommended Additional Visual Inspection (not mandated by the Standard):
	
	Yes
	No
	N/A

	Dead-front panel(s) in place & as per manufacturer’s specification.
	
	 FORMCHECKBOX 

	 FORMCHECKBOX 

	 FORMCHECKBOX 


	Circuit disconnect means painted RED and locked “on”.
	
	 FORMCHECKBOX 

	 FORMCHECKBOX 

	 FORMCHECKBOX 


	Power supply cabinet (where applicable) is clean and free of dust and dirt.
	
	 FORMCHECKBOX 

	 FORMCHECKBOX 

	 FORMCHECKBOX 


	C5.7 Emergency Power Supply Test And Inspection

	 Emergency Power Supply Field Location:
	
	

	Emergency Power Supply Identification:
	
	

	Battery Type (as installed):  
	 FORMCHECKBOX 
 Sealed Lead Acid    FORMCHECKBOX 
 Ni-Cad     FORMCHECKBOX 
 Lithium-Ion     FORMCHECKBOX 
 Wet Lead
	

	Battery Capacity (as installed):
	
	AH
	
	

	Required Building Code Alarm Operation:  
	 FORMCHECKBOX 
 30 minutes       FORMCHECKBOX 
 120 minutes
	
	

	
	Yes
	No
	N/A

	A
	Correct battery type as recommended by the manufacturer.
	
	 FORMCHECKBOX 

	 FORMCHECKBOX 

	

	B
	Correct battery rating as determined by battery calculations based on full system load.
	
	 FORMCHECKBOX 

	 FORMCHECKBOX 

	 FORMCHECKBOX 


	C
	Battery voltage (main power “on”):
	
	VDC
	
	
	

	D
	Battery voltage – main power “off” – FAS in supervisory condition:
	
	VDC
	
	
	

	
	Battery current  - main power “off” – FAS in supervisory condition:
	
	mA
	
	
	

	E
	Battery voltage – main power “off” – FAS in full load ALARM:
	
	VDC
	
	
	

	
	Battery current – main power “off” – FAS in full load ALARM:
	
	A
	
	
	

	F
	Battery charging current (main power “on”):
	
	mA
	
	
	

	G
	Inspected for physical damage.
	
	 FORMCHECKBOX 

	 FORMCHECKBOX 

	 FORMCHECKBOX 


	H
	Terminals cleaned and lubricated.
	
	 FORMCHECKBOX 

	 FORMCHECKBOX 

	 FORMCHECKBOX 


	I
	Terminals clamped tightly.
	
	 FORMCHECKBOX 

	 FORMCHECKBOX 

	 FORMCHECKBOX 


	J
	Correct electrolyte level.
	
	 FORMCHECKBOX 

	 FORMCHECKBOX 

	 FORMCHECKBOX 


	K
	Specific gravity of the electrolyte is within the battery manufacturer’s specifications.
	
	 FORMCHECKBOX 

	 FORMCHECKBOX 

	 FORMCHECKBOX 


	L
	Inspected for electrolyte leakage.
	
	 FORMCHECKBOX 

	 FORMCHECKBOX 

	 FORMCHECKBOX 


	M
	Adequately ventilated.
	
	 FORMCHECKBOX 

	 FORMCHECKBOX 

	 FORMCHECKBOX 


	N
	Record manufacturer’s date code or in-service date:
	
	
	
	

	O
	Disconnection causes trouble signal.
	
	 FORMCHECKBOX 

	 FORMCHECKBOX 

	 FORMCHECKBOX 


	P
	Indicate type of tests performed on a fully charged battery:
	
	
	
	

	
	(i)
	Required supervisory load for 24 h followed by the required full load operation
	
	 FORMCHECKBOX 

	 FORMCHECKBOX 

	 FORMCHECKBOX 


	
	(ii)
	Silent test using load resistor method for full duration test (refer to Appendix D1)
	
	 FORMCHECKBOX 

	 FORMCHECKBOX 

	 FORMCHECKBOX 


	
	(iii)
	Silent accelerated test (refer to Appendix D2)
	
	 FORMCHECKBOX 

	 FORMCHECKBOX 

	 FORMCHECKBOX 


	Q
	Record calculated battery capacity (refer to Appendix D3.1-C).
	
	AH
	
	
	

	R
	Record the battery terminal voltage after tests are completed.
	
	VDC
	
	
	

	S
	Battery voltage not less than 85% of its rated capacity after tests completed.
	
	 FORMCHECKBOX 

	 FORMCHECKBOX 

	 FORMCHECKBOX 


	T
	Generator provides power to the AC circuit serving the fire alarm system.
	
	 FORMCHECKBOX 

	 FORMCHECKBOX 

	 FORMCHECKBOX 


	U
	Trouble condition at the emergency generator results in an audible common trouble signal and a visual indication at the required annunciator.
	
	 FORMCHECKBOX 

	 FORMCHECKBOX 

	 FORMCHECKBOX 


	Recommended Additional Inspection (not mandated by the Standard):

	Generator fueled by:   FORMCHECKBOX 
 Diesel      FORMCHECKBOX 
  Natural Gas     FORMCHECKBOX 
 Other:
	
	

	Fuel Level:
	
	% of full capacity
	Estimated run time:
	
	Hours


	C5.8 ANNUNCIATOR AND DISPLAY AND CONTROL CENTRE TEST AND INSPECTION

	Annunciator Location:
	
	

	Annunciator Identification:
	
	

	
	Yes
	No
	N/A

	A
	Power “on” indicator operates.
	
	 FORMCHECKBOX 

	 FORMCHECKBOX 

	 FORMCHECKBOX 


	B
	Individual alarm and supervisory input zone clearly indicated and separately designated.
	
	 FORMCHECKBOX 

	 FORMCHECKBOX 

	 FORMCHECKBOX 


	C
	Individual alarm and supervisory input zone designation labels are properly identified.
	
	 FORMCHECKBOX 

	 FORMCHECKBOX 

	 FORMCHECKBOX 


	D
	Where active and supporting field devices are utilized, device labels correspond with actual field location.
	
	 FORMCHECKBOX 

	 FORMCHECKBOX 

	 FORMCHECKBOX 


	E
	Common trouble signal operates.
	
	 FORMCHECKBOX 

	 FORMCHECKBOX 

	 FORMCHECKBOX 


	F
	Visual indicator test (lamp test) operates.
	
	 FORMCHECKBOX 

	 FORMCHECKBOX 

	 FORMCHECKBOX 


	G
	Input wiring from control unit or transponder is supervised and of the correct type and gauge in accordance with the equipment manufacturer’s installation wiring requirements.
	
	 FORMCHECKBOX 

	 FORMCHECKBOX 

	 FORMCHECKBOX 


	H
	Alarm signal silence visual indicator operates.
	
	 FORMCHECKBOX 

	 FORMCHECKBOX 

	 FORMCHECKBOX 


	I
	Switches for ancillary functions operate as per design and specification.
	
	 FORMCHECKBOX 

	 FORMCHECKBOX 

	 FORMCHECKBOX 


	J
	Ancillary functions visual indicators operates.
	
	 FORMCHECKBOX 

	 FORMCHECKBOX 

	 FORMCHECKBOX 


	K
	Manual activation of alarm signal and indication operates.
	
	 FORMCHECKBOX 

	 FORMCHECKBOX 

	 FORMCHECKBOX 


	L
	Displays are visible in the installed location.
	
	 FORMCHECKBOX 

	 FORMCHECKBOX 

	 FORMCHECKBOX 


	M
	Operates on emergency power.
	
	 FORMCHECKBOX 

	 FORMCHECKBOX 

	 FORMCHECKBOX 


	N
	Visual indicators comply with Table 3 – Visual indicators Colour Code
	
	 FORMCHECKBOX 

	 FORMCHECKBOX 

	 FORMCHECKBOX 


	O
	Multi-line sequential display operates as per Appendix C5.9 (Annunciators or Sequential Displays), where utilized.
	
	 FORMCHECKBOX 

	 FORMCHECKBOX 

	 FORMCHECKBOX 


	C5.9 ANNUNCIATORS OR SEQUENTIAL DISPLAYS

	Annunciator/Sequential Display Location:
	
	

	Annunciator/Sequential Display  Identification:
	
	

	
	Yes
	No
	N/A

	A
	Power “on” indicator operates.
	
	 FORMCHECKBOX 

	 FORMCHECKBOX 

	 FORMCHECKBOX 


	B
	Individual alarm and supervisory zone indication operates.
	
	 FORMCHECKBOX 

	 FORMCHECKBOX 

	 FORMCHECKBOX 


	
	Exception:  Operation of each individual alarm and supervisory zone indication gives the identical indication, or lights the identical indicators at the other annunciator(s) and sequential display(s).
	
	 FORMCHECKBOX 

	 FORMCHECKBOX 

	 FORMCHECKBOX 


	
	Specify method of confirmation:
	
	
	
	
	

	
	Minimum of one alarm zone and one supervisory zone tested per annunciator or sequential display to confirm operation.
	
	 FORMCHECKBOX 

	 FORMCHECKBOX 

	 FORMCHECKBOX 


	C
	Individual alarm and supervisory input zone designation labels are properly identified.
	
	 FORMCHECKBOX 

	 FORMCHECKBOX 

	 FORMCHECKBOX 


	D
	Where active and supporting field devices are utilized, device labels correspond with actual field location.
	
	 FORMCHECKBOX 

	 FORMCHECKBOX 

	 FORMCHECKBOX 


	E
	Common trouble signal operates.
	
	 FORMCHECKBOX 

	 FORMCHECKBOX 

	 FORMCHECKBOX 


	F
	Visual indicator test (lamp test) operates.
	
	 FORMCHECKBOX 

	 FORMCHECKBOX 

	 FORMCHECKBOX 


	G
	Input wiring from control unit or transponder is supervised and of the correct type and gauge in accordance with the equipment manufacturer’s installation wiring requirements.
	
	 FORMCHECKBOX 

	 FORMCHECKBOX 

	 FORMCHECKBOX 


	H
	Alarm signal silence visual indicator operates.
	
	 FORMCHECKBOX 

	 FORMCHECKBOX 

	 FORMCHECKBOX 


	I
	Switches for ancillary functions operate as per design and specification.
	
	 FORMCHECKBOX 

	 FORMCHECKBOX 

	 FORMCHECKBOX 


	J
	Ancillary functions visual indicators operates.
	
	 FORMCHECKBOX 

	 FORMCHECKBOX 

	 FORMCHECKBOX 


	K
	Manual activation of alarm signal and indication operates.
	
	 FORMCHECKBOX 

	 FORMCHECKBOX 

	 FORMCHECKBOX 


	L
	Displays are visible in the installed location.
	
	 FORMCHECKBOX 

	 FORMCHECKBOX 

	 FORMCHECKBOX 


	C5.10 Remote Trouble Signal Unit Test And Inspection

	Remote trouble signal unit location:
	
	

	Remote trouble signal unit identification:
	
	

	
	Yes
	No
	N/A

	A
	Input wiring from control unit or transponder is supervised.
	
	 FORMCHECKBOX 

	 FORMCHECKBOX 

	 FORMCHECKBOX 


	B
	Visual trouble signal operates.
	
	 FORMCHECKBOX 

	 FORMCHECKBOX 

	 FORMCHECKBOX 


	C
	Audible trouble signal operates.
	
	 FORMCHECKBOX 

	 FORMCHECKBOX 

	 FORMCHECKBOX 


	D
	Audible trouble signal silence operates.
	
	 FORMCHECKBOX 

	 FORMCHECKBOX 

	 FORMCHECKBOX 



	C5.11 Printer Test

	Printer Location:
	
	

	Printer Identification:
	
	

	
	Yes
	No
	N/A

	A
	Operates as per design and specification
	
	 FORMCHECKBOX 

	 FORMCHECKBOX 

	 FORMCHECKBOX 


	B
	Zone of each alarm initiating device is correctly printed.
	
	 FORMCHECKBOX 

	 FORMCHECKBOX 

	 FORMCHECKBOX 


	C
	Rated voltage is present.
	
	 FORMCHECKBOX 

	 FORMCHECKBOX 

	 FORMCHECKBOX 



	C5.12 Ancillary Device Circuit Test

	Record Specific Type of Ancillary Circuit
	Operation of Ancillary Circuit Confirmed

	
	Yes
	No
	N/A

	
	 FORMCHECKBOX 

	 FORMCHECKBOX 

	 FORMCHECKBOX 


	
	 FORMCHECKBOX 

	 FORMCHECKBOX 

	 FORMCHECKBOX 


	
	 FORMCHECKBOX 

	 FORMCHECKBOX 

	 FORMCHECKBOX 


	
	 FORMCHECKBOX 

	 FORMCHECKBOX 

	 FORMCHECKBOX 


	
	 FORMCHECKBOX 

	 FORMCHECKBOX 

	 FORMCHECKBOX 


	
	 FORMCHECKBOX 

	 FORMCHECKBOX 

	 FORMCHECKBOX 


	
	 FORMCHECKBOX 

	 FORMCHECKBOX 

	 FORMCHECKBOX 


	
	 FORMCHECKBOX 

	 FORMCHECKBOX 

	 FORMCHECKBOX 


	
	 FORMCHECKBOX 

	 FORMCHECKBOX 

	 FORMCHECKBOX 


	
	 FORMCHECKBOX 

	 FORMCHECKBOX 

	 FORMCHECKBOX 


	
	 FORMCHECKBOX 

	 FORMCHECKBOX 

	 FORMCHECKBOX 


	
	 FORMCHECKBOX 

	 FORMCHECKBOX 

	 FORMCHECKBOX 


	
	 FORMCHECKBOX 

	 FORMCHECKBOX 

	 FORMCHECKBOX 


	
	 FORMCHECKBOX 

	 FORMCHECKBOX 

	 FORMCHECKBOX 


	
	 FORMCHECKBOX 

	 FORMCHECKBOX 

	 FORMCHECKBOX 


	
	 FORMCHECKBOX 

	 FORMCHECKBOX 

	 FORMCHECKBOX 


	
	 FORMCHECKBOX 

	 FORMCHECKBOX 

	 FORMCHECKBOX 


	
	 FORMCHECKBOX 

	 FORMCHECKBOX 

	 FORMCHECKBOX 


	
	 FORMCHECKBOX 

	 FORMCHECKBOX 

	 FORMCHECKBOX 


	
	 FORMCHECKBOX 

	 FORMCHECKBOX 

	 FORMCHECKBOX 


	
	 FORMCHECKBOX 

	 FORMCHECKBOX 

	 FORMCHECKBOX 


	
	 FORMCHECKBOX 

	 FORMCHECKBOX 

	 FORMCHECKBOX 


	
	 FORMCHECKBOX 

	 FORMCHECKBOX 

	 FORMCHECKBOX 


	
	 FORMCHECKBOX 

	 FORMCHECKBOX 

	 FORMCHECKBOX 


	
	 FORMCHECKBOX 

	 FORMCHECKBOX 

	 FORMCHECKBOX 


	
	 FORMCHECKBOX 

	 FORMCHECKBOX 

	 FORMCHECKBOX 


	
	 FORMCHECKBOX 

	 FORMCHECKBOX 

	 FORMCHECKBOX 


	
	 FORMCHECKBOX 

	 FORMCHECKBOX 

	 FORMCHECKBOX 


	
	 FORMCHECKBOX 

	 FORMCHECKBOX 

	 FORMCHECKBOX 


	
	 FORMCHECKBOX 

	 FORMCHECKBOX 

	 FORMCHECKBOX 


	
	 FORMCHECKBOX 

	 FORMCHECKBOX 

	 FORMCHECKBOX 


	
	 FORMCHECKBOX 

	 FORMCHECKBOX 

	 FORMCHECKBOX 


	
	 FORMCHECKBOX 

	 FORMCHECKBOX 

	 FORMCHECKBOX 


	
	 FORMCHECKBOX 

	 FORMCHECKBOX 

	 FORMCHECKBOX 


	
	 FORMCHECKBOX 

	 FORMCHECKBOX 

	 FORMCHECKBOX 



Note:  The tests reported on this form do not include the actual operational test of ancillary devices except where noted.
	C5.13 Interconnection to the Fire Signal Receiving Centre

	Communicator Location:
	
	

	Circuit Disconnect Means Location:
	
	

	Circuit Panel/Breaker Identification:
	
	

	
	Yes
	No
	N/A

	A
	The fire signal receiving centre transmitter is integral to the fire alarm control unit.
	
	 FORMCHECKBOX 

	 FORMCHECKBOX 

	

	B
	The fire signal receiving centre transmitter is located remotely from the fire alarm control unit.
	
	 FORMCHECKBOX 

	 FORMCHECKBOX 

	

	C
	Where an interconnection between the fire alarm control unit and a separate fire signal receiving centre transmitter is provided, a demarcation terminal box with a minimum of twelve (12) terminals is installed.
	
	 FORMCHECKBOX 

	 FORMCHECKBOX 

	 FORMCHECKBOX 


	D
	The demarcation terminal box is located in the same room as the fire alarm control unit it is connected to.
	
	 FORMCHECKBOX 

	 FORMCHECKBOX 

	 FORMCHECKBOX 


	E
	The demarcation terminal box is labeled “Fire Alarm Demarcation” and/or “Limitation D’Alarme Incendie”.
	
	 FORMCHECKBOX 

	 FORMCHECKBOX 

	 FORMCHECKBOX 


	F
	The conductors installed between the fire alarm control panel and the demarcation terminal box complies with Section 3.4 of CAN/ULC-S524-06.
	
	 FORMCHECKBOX 

	 FORMCHECKBOX 

	 FORMCHECKBOX 


	G
	Tested and confirmed operation of alarm relay.
	
	 FORMCHECKBOX 

	 FORMCHECKBOX 

	 FORMCHECKBOX 


	H
	Tested and confirmed operation of trouble relay.
	
	 FORMCHECKBOX 

	 FORMCHECKBOX 

	 FORMCHECKBOX 


	I
	Tested and confirmed operation of supervisory relay.
	
	 FORMCHECKBOX 

	 FORMCHECKBOX 

	 FORMCHECKBOX 


	J
	Confirm that the alarm transmission to the fire signal receiving centre is received.
	
	 FORMCHECKBOX 

	 FORMCHECKBOX 

	 FORMCHECKBOX 


	K
	Confirm that the supervisory transmission to the fire signal receiving centre is received.
	
	 FORMCHECKBOX 

	 FORMCHECKBOX 

	 FORMCHECKBOX 


	L
	Confirm that the trouble transmission to the fire signal receiving centre is received.
	
	 FORMCHECKBOX 

	 FORMCHECKBOX 

	 FORMCHECKBOX 


	M
	Record the name and telephone number of the fire signal receiving centre.
	
	
	

	
	Company:
	
	Telephone:
	
	
	
	
	
	

	
	Address:
	
	
	
	

	N
	Operation of the fire signal receiving centre transmitter bypass means results in a specific trouble indication at the fire alarm control unit or transponder and transmits a trouble signal to the fire signal receiving centre.
	
	 FORMCHECKBOX 

	 FORMCHECKBOX 

	 FORMCHECKBOX 


	Additional Information (not mandated by the Standard):
	Yes
	No
	N/A

	The communicator installed in accordance with CAN/ULC-S561-13.
	
	 FORMCHECKBOX 

	 FORMCHECKBOX 

	 FORMCHECKBOX 


	The fire signal receiving centre is ULC Listed.
	
	 FORMCHECKBOX 

	 FORMCHECKBOX 

	 FORMCHECKBOX 


	The fire signal receiving centre ULC certification number is:
	
	
	
	

	The communicator is being tested in accordance with CAN/ULC-S561-13.  

Supporting documentation attesting to this is on site and has been reviewed.
	
	 FORMCHECKBOX 

 FORMCHECKBOX 

	 FORMCHECKBOX 

 FORMCHECKBOX 

	 FORMCHECKBOX 

 FORMCHECKBOX 


	The ULC “Central Station Fire Protective Signalling Service” Certificate is valid.
	
	 FORMCHECKBOX 

	 FORMCHECKBOX 

	 FORMCHECKBOX 


	The ULC “Central Station Fire Protective Signalling Service” Certificate expires on:
	
	

	The last inspection noted on the Certificate occurred on:
	
	

	The communicator has been reset following completion of testing.
	
	 FORMCHECKBOX 

	 FORMCHECKBOX 

	 FORMCHECKBOX 


	The communicator has been placed back into service.
	
	 FORMCHECKBOX 

	 FORMCHECKBOX 

	 FORMCHECKBOX 


	The communicator is trouble free.
	
	 FORMCHECKBOX 

	 FORMCHECKBOX 

	 FORMCHECKBOX 



	ADDITIONAL NOTES:

4. Smoke detector sensitivity measurement should be recorded in the “Remarks” column of the Individual Device Test Record.  Analog smoke detectors may report their obscuration level (sensitivity) to the fire alarm’s common control.  This information should be retrieved and recorded in the “Remarks” column.

5. Status change, including time delay (where applicable), should be recorded in the “Remarks” column.

6. Duct smoke detector pressure differential should be confirmed and recorded in the “Remarks” column.  Detector tubes must be pulled and their alignment confirmed if results indicate any abnormalities.  Record any discrepancies in the “Remarks” column.  
7. Time delay setting of water flow switch should be recorded in the “Remarks” column.

8. Sprinkler supervisory switches should cause a “trouble” condition to be annunciated.  This should be a latching type trouble (or “supervisory trouble”) only restorable by pressing “Reset” on the fire alarm control panel.  Exceptions must be noted in “Comments”.

9. Upper and lower pressure setting of supervisory devices should be recorded in the “Remarks” column.

10. Low temperature setting should be recorded in the “Remarks” column.

11. Identify the specific ancillary devices in the “Remarks” column.

12. Where possible, identify the date a fire detector is changed.  If housing discolouration is noted, attempt to identify the source and note the date of manufacture.  Heat detectors whose labels are missing, faded and unreadable, or painted are considered failed and require replacement.  This information should be noted in the “Remarks” column.

13. Identify type and function of each addressable device in the “Remarks” column.

14. Exposure to charging currents in excess of 100 mA will significantly shorten the service life of Ni-Cad and sealed lead acid batteries.

15. Relays tied to listed fire alarm equipment initiating/supervisory circuits must be properly supervised.  Note exceptions in “Comments”.

16. The system’s documentation should provide information concerning the number of addressable devices that are connected to each isolator.  Ensure this number does not exceed the Manufacturer’s requirements.  Any exceptions should be noted in “Comments”.

17. The building owner/manager must maintain the records for the Verification on site for inspection by the local authority.

18. Operation of each annunciator or sequential display must be confirmed visually.

19. Stand-by batteries that are remotely located more than twelve (12) meters from the Fire Alarm Common Control must be fused (or installed in accordance with the manufacturer’s recommendations or requirements).


Any exceptions to the above are noted in the “Remarks/Comments” area on the last page of this report.

	C6.1 Field Device Testing - LEGEND

	Device
	Description
	Type
	Model Number

	
	Manual Initiating Devices
	
	

	M
	Manual pull station
	
	

	MAS
	Manual Abort Station
	
	

	
	Automatic Fire Detection Devices
	
	

	HD
	Heat Detector, restorable or non-restorable, fixed temperature  (12)
	
	

	RHD
	Heat Detector, restorable, rate-of-rise thermostat   (12)
	
	

	S
	Ionization Smoke detector  (4)
	
	

	
	Sensitivity Test Method (or Test Equipment Model/Method):
	
	

	
	
	
	

	
	Manufacturer’s Sensitivity Test Range:
	
	

	
	
	
	

	PS
	Photo-electric Smoke detector   (4)
	
	

	
	Sensitivity Test Method (or Test Equipment Model/Method):
	
	

	
	
	
	

	
	Manufacturer’s Sensitivity Test Range:
	
	

	
	
	
	

	DS
	Duct Smoke detector   (4, 5, 6)
	
	

	
	Sensitivity Test Method (or Test Equipment Model/Method):
	
	

	
	
	
	

	
	Manufacturer’s Sensitivity Test Range:
	
	

	
	
	
	

	MC
	Multi-Criteria type detector (specify detection types)
	
	

	
	Sensitivity Test Method (or Test Equipment Model/Method):
	
	

	
	
	
	

	
	Manufacturer’s Sensitivity Test Range:
	
	

	
	
	
	

	CO
	Carbon Monoxide detector
	
	

	OD
	Other Detector type (specify)
	
	

	EOL(R)
	End-of-Line resistor (“R” indicates “Power Supervision Relay”)
	
	

	
	Fire Sprinkler Devices
	
	

	FS
	Sprinkler Flow Switch   (7)
	
	

	FPS
	Sprinkler Flow Pressure Switch   (7)
	
	

	TS
	Sprinkler valve supervisory Tamper Switch  (8)
	
	

	LA
	Low Air supervisory device   (9)
	
	

	LT
	Low Temperature supervisory device   (10)
	
	

	HTC
	Heat Trace Controller
	
	

	TLW
	Tank Low Water supervisory device
	
	

	
	Fire Alarm Signalling Devices
	
	

	B
	Bell
	
	

	H
	Horn
	
	

	BZ(S)
	Mini Buzzer (“S” indicates “silenceable” type)
	
	

	SSB
	Smoke Sounder Base
	
	

	V
	Visual alarm device (specify strobe type or corridor indicator)
	
	

	SP
	Cone type Speaker
	
	

	HSP
	Horn Speaker
	
	

	AV
	Combination Audible/Visual Device - specify type (i.e. Horn/Strobe Unit)
	
	

	SCIM
	Signal Circuit Isolation Module
	
	

	ET
	Emergency Telephone (Fire Fighter’s Phone)
	
	

	
	Supporting Field Devices (Addressable Systems)
	
	

	RPM
	Remote Point Module (13)
	
	

	SRIM
	Single point Remote Initiating Module
	
	

	DRIM
	Dual input Remote Initiating Module
	
	

	RPIM
	Remote Point Isolator Module  (16)
	
	

	SCRM
	Signal Circuit Remote Module
	
	

	RRM(S)
	Remote Relay Module (“S” provides supervised outputs)
	
	

	
	Ancillary Devices
	
	

	DH(M,FL)
	Door Holder (“M” is Magnetic, “FL” is Fusible Link)
	
	

	DM
	Damper Motor
	
	

	R
	Relay
	
	

	AD
	Other Ancillary Device   (11)
	
	

	SA
	Smoke Alarm (specify single or multi-station type)
	
	


C6.2 Individual Device Record

	Column Legend

	A

B

C
	Correctly installed

Unit requires service, repair, missing, or cleaning

Alarm operation confirmed
	D

E

F

G
	Annunciator indication confirmed 

Circuit number or address 

Supervision and ground fault detection

Smoke detector sensitivity


“( “  Yes - Acceptable    “X”  No – Unacceptable (Explain NO answers in comments)    “Dash” - Not applicable

	Location
	Device
	A
	B
	C
	D
	E
	F
	G
	Remarks

	
	
	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	
	
	


C6.3 SIGNALLING DEVICE SOUND LEVEL MEASUREMENT

(Reference: Clause 5.10.1-C)

	Zone
	Location/Description
	Ambient dBA
	Alarm dBA
	Remarks

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	
	


	Remarks/Comments

	


C6.4 SIGNALLING DEVICE INTELLIGIBILITY MEASUREMENT

(Reference: CAN/ULC-S537-13 Clause 6.10.1-C and 6.10.1-G, NBCC 2010 Sentence 3.2.4.22-2)

	Zone
	Location/Description
	Intelligibility CIS
	Remarks

	
	
	
	

	
	
	
	

	
	
	
	

	
	
	
	

	
	
	
	

	
	
	
	

	
	
	
	

	
	
	
	

	
	
	
	

	
	
	
	

	
	
	
	

	
	
	
	

	
	
	
	

	
	
	
	

	
	
	
	

	
	
	
	

	
	
	
	

	
	
	
	

	
	
	
	

	
	
	
	

	
	
	
	

	
	
	
	

	
	
	
	

	
	
	
	

	
	
	
	

	
	
	
	

	
	
	
	

	
	
	
	

	
	
	
	


	Remarks/Comments

	


	C6.5 Deficiencies

	


	C6.6 Recommendations

	


	C6.7 Remarks

	


www.firetechs.net  (Form 537-04 Version 16.3)                                                                                                                                                    
www.firetechs.net  (Form 537-04 Version 16.3)                                                                                                                                                     Page 2 of 18

