## EDWARDS (GE)
|  | EDWARDS/GE Panel Model Number | 1527 | 2280 | 6601 | 6602/6604 | 6616/6632 | EST1-1Z1 | EST1-2Z3/2Z6 | ESA | 6500 | 8500 (IDC) | 8500 (ZAM) 4 wire | 8500 ESAC | IRC3 (ZB8) | IRC3 (RZB) NV | IRC3 (SIGA-UM) V | IRC 3 (SIGA-UM) NV | EST2 (SIGA-UM) | EST3 (IDC) | EST3 (SIGA-UM)
| Smoke Detector Model Number | Base
System Sensor
| 1400 | NA | X | X | √ | √ | √ | √ | √ | √ | X | √⁴ | √ | √⁴ | X | √ | √ | √ | √ | √ | √
| 2400 | NA | X | X | X | X | X | X | X | X | X | X | X | X | X | X | X | X | X | X | X
| 1151¹ | EDWB110LP | X | X | √ | √ | √ | √ | √ | √ | X | √ | √ | √ | √ | √ | √ | √ | √ | √ | √
| 1151¹ | EDWB116LP(RLY) | X | X | X | X | √ | X | X | X | X | √ | √ | √ | √ | √ | √ | √ | √ | √ | √
| 1151¹ | EDWB110RLP | X | X | X | X | X | X | X | √ | √ | X | X | X | X | X | X | X | X | X | X
| 2151¹ | EDWB110LP | X | X | √ | √ | √ | √ | √ | √ | X | √ | √ | √ | √ | √ | √ | √ | √ | √ | √
| 2151¹ | EDWB116LP(RLY) | X | X | X | X | √ | X | X | X | X | √ | √ | √ | √ | √ | √ | √ | √ | √ | √
| 2151¹ | EDWB110RLP | X | X | X | X | X | X | X | √ | √ | X | X | X | X | X | X | X | X | X | X
| 1451¹ | EDWB401B | X | X | √ | √ | √ | √ | √ | X | X | √ | √ | √ | √ | √ | √ | √ | √ | √ | √
| 1451¹ | EDWB406B(RLY) | X | X | X | X | √ | X | √ | X | X | √ | X | √ | √ | √ | √ | √ | √ | √ | √
| 1451¹ | EDWB401BR | X | X | X | X | X | X | X | √ | √ | X | X | X | X | X | X | X | X | X | X
| 1451¹ | EDWB406BR(RLY) | X | X | X | X | √ | X | √ | √ | √ | X | X | X | √ | √ | √ | X | X | X | X
| 2451¹ | EDWB401B | X | X | √ | √ | √ | √ | √ | X | X | √ | √ | √ | √ | √ | √ | √ | √ | √ | √
| 2451¹ | EDWB406B(RLY) | X | X | X | X | √ | X | √ | X | X | √ | √ | √ | √ | √ | √ | √ | √ | √ | √
| 2451¹ | EDWB401BR | X | X | X | X | √ | X | √ | X | X | X | X | √ | √ | √ | √ | √ | √ | √ | √
| 2451¹ | EDWB406BR(RLY) | X | X | X | X | X | X | X | √ | √ | X | X | X | X | X | X | X | X | X | X
| C2W-BA | NA | X | X | X | X | X | X | X | X | X | X | X | X | X | X | X | X | X | X | X
GE/Edwards
| C2M-PD1² | NA | √² | √² | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √ | √
| C2M-PDC³ | NA | X | X | √³ | √³ | √³ | √³ | √³ | √³ | √³ | √³ | √³ | √³ | √³ | √³ | √³ | √³ | √³ | √³ | X
| C2M-PDHC³ | NA | X | X | √³ | √³ | √³ | √³ | √³ | √³ | √³ | √³ | √³ | √³ | √³ | √³ | √³ | √³ | √³ | √³ | X
| C2M-PDHRC³ | NA | X | X | √³ | √³ | √³ | √³ | √³ | X | √³ | √³ | X | √³ | √³ | √³ | √³ | √³ | √³ | √³ | X
| Max Number of Detectors/Circuit |  | NA | NA | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30⁴ | 30 | 30⁴ | 30 | 30 | 30 | 30 | 30 | 30 | 30
| Max Number of C2M Series/Circuit |  | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30⁴ | 30 | 30⁴ | 30 | 30 | 30 | 30 | 30 | 30 | 30
Legend: | √ = Compatible | V = VERIFIED
| X = Not Compatible | NV = NONE VERIFIED
Notes: | (1) Must use specified base (do not substitute with System Sensor branded bases)
(2) C2M-PD1 is a direct replacement for Edwards Models 6249C & 6251C and may be used on all panels where these detectors were cross-listed (C2M-PDC has "Clean Me" technology and may NOT function with some panel models)
(3) Compatible only with "Clean Me" option "OFF"
(4) Do NOT mix model 1400 and 2400 smoke detectors on the same circuit
(5) EDWB110RLP and EDWB401BR both contain current limiting resistors and are for use with specified panels only
(6) Each detection circuit must employ a single model number of smoke detector (does not apply to detectors employing plug-in bases) - DO NOT MIX TECHNOLOGIES
Compatibility Issues: | 1. Is there a remote LED indicator?
2. Does the smoke detector have a relay base?
3. Check total number of detectors on a circuit does not exceed the recommended maximum.
Copyright © 2008 by Frank Kurz (All Rights Reserved)

## MIRTONE (GE)
|  | Mirtone Panel Model Number | 7124 | 7200 | 7600 | 7800 | 7501 | 7502/7504 | 7516/7532 | MIR1-1Z1 | MIR1-2Z3/2Z6 | FS-101 | FS-302 | FS-502 | FS-1004 | M2000 | MIR2 (GSA-UM) | 790 (79045, 79045-2) | 8000
| Smoke Detector Model Number | Base
System Sensor
| 1400 | NA | X | √ | √ | √ | √ | √ | √ | √ | √ | √⁴(30) | √⁴(15) | √⁴(15) | √⁴(15) | √ | √ | √⁴ | √
| 2400 | NA | X | X | X | X | X | X | X | X | X | √⁴(25) | √⁴(12) | √⁴(12) | √⁴(12) | √ | X | X | X
| 1151¹ | MTB110LP | X | X | X | X | X | X | X | X | √ | √⁴(30) | √⁴(15) | √⁴(15) | √⁴(15) | X | √ | X | √
| 1151¹ | MTB116LP(RLY) | X | X | X | X | X | X | √ | X | X | X | X | X | X | X | √ | X | √
| 1151¹ | MTB110RLP | X | X | X | X | √ | √ | √ | X | X | X | X | X | X | √ | X | X | X
| 2151¹ | MTB110LP | X | X | X | X | √ | √ | √ | √ | √ | √⁴(25) | √⁴(12) | √⁴(12) | √⁴(12) | √ | √ | X | X
| 2151¹ | MTB116LP(RLY) | X | X | X | X | X | X | √ | X | X | X | X | X | X | X | √ | X | √
| 2151¹ | MTB110RLP | X | X | X | X | X | X | X | X | X | X | X | X | X | √ | X | X | X
| 1451¹ | MTB401B | X | X | X | X | √ | √ | √ | √ | √ | √⁴(30) | √⁴(15) | √⁴(15) | √⁴(15) | X | √ | X | √
| 1451¹ | MTB406B(RLY) | X | X | X | X | X | X | √ | X | √ | X | X | X | X | X | √ | X | √
| 1451¹ | MTB401BR | X | X | X | X | X | X | X | X | X | X | X | X | X | √ | X | X | X
| 1451¹ | MTB406BR(RLY) | X | X | X | X | X | X | √ | X | X | X | X | X | X | √ | X | X | X
| 2451¹ | MTB401B | X | X | X | X | √ | √ | √ | √ | √ | √⁴(25) | √⁴(12) | √⁴(12) | √⁴(12) | X | √ | X | √
| 2451¹ | MTB406B(RLY) | X | X | X | X | X | X | X | X | X | X | X | X | X | X | √ | X | √
| 2451¹ | MTB401BR | X | X | X | X | X | X | X | X | X | X | X | X | X | √ | X | X | √
| 2451¹ | MTB406BR(RLY) | X | X | X | X | X | X | X | X | X | X | X | X | X | √ | X | X | X
| C2W-BA | NA | X | X | X | X | X | X | X | X | X | X | X | X | X | X | X | X | X
GE/Mirtone
| CM2M-PD1² | NA | X | X | X | X | √ | √ | √ | √ | √ | √(42) | √(21) | √(21) | √(21) | √ | √ | X | √
| CM2M-PDC³ | NA | X | X | X | X | √³ | √³ | √³ | √³ | √³ | √³(42) | √³(21) | √³(21) | √³(21) | √³ | √³ | X | √³
| CM2M-PDHC³ | NA | X | X | X | X | √³ | √³ | √³ | √³ | √³ | √³(42) | √³(21) | √³(21) | √³(21) | √³ | √³ | X | √³
| CM2M-PDHRC³ | NA | X | X | X | X | √³ | √³ | √³ | √³ | √³ | √³(30) | √³(21) | √³(21) | √³(21) | X | √³ | X | √³
| Max Number of Detectors/Circuit |  | NA | 20 | 20 | 20 | 30 | 30 | 30 | 30 | 30 | SPL⁴ | SPL⁴ | SPL⁴ | SPL⁴ | 30 | 30 | 20 | 30
| Max Number of CM2M Series/Circuit |  | NA | NA | NA | NA | 30 | 30 | 30 | 30 | 30 | SPL⁴ | SPL⁴ | SPL⁴ | SPL⁴ | 30 | 30 | NA | 30
Legend: | √ = Compatible
X = Not Compatible
Notes: | (1) Must use specified base (do not substitute with System Sensor branded bases)
(2) CM2M-PD1 is a direct replacement for Edwards Models 6249C & 6251C and may be used on all panels where these detectors were cross-listed (CM2M-PDC has "Clean Me" technology and may NOT function with some panel models)
(3) Compatible only with "Clean Me" option "OFF"
(4) Do NOT mix model 1400 and 2400 smoke detectors on the same circuit with System Sensor 1151/1451 or System Sensor 2151/2451
(5) MTB110RLP and MTB401BR both contain current limiting resistors and are for use with specified panels only
(6) Each detection circuit must employ a single model number of smoke detector - DO NOT MIX TECHNOLOGIES and observe limit numbers.
Compatibility Issues: | 1. Is there a remote LED indicator?
2. Does the smoke detector have a relay base?
3. Check total number of detectors on a circuit does not exceed the recommended maximum.
4. In instances where there are NO detectors listed, the control panel must be changed and the entire fire alarm system verified.
Copyright © 2008 by Frank Kurz (All Rights Reserved)

## Mircom
| Compatible Analog Loop Devices | Mircom Panel Model Number | FX-2000 | FA-300 | FA-100 | FA-200 | FA-1000
Mircom
| MIX-1551A | NA | √ | X | X | X | X
| MIX-2551A | NA | √ | X | X | X | X
| MIX-1251A | NA | √ | X | X | X | X
| MIX-2251A/2251TA | NA | √ | X | X | X | X
| MIX-2551TMA | NA | √ | X | X | X | X
| MIX-7251A | NA | √ | X | X | X | X
| MIX-M500MA | NA | √ | X | X | X | X
| MIX-M501MA | NA | √ | X | X | X | X
| MIX-1251BA | NA | √ | X | X | X | X
| MIX-2251BA | NA | √ | X | X | X | X
| MIX-2251TMBA | NA | √ | X | X | X | X
| MIX-2251TBA | NA | √ | X | X | X | X
| MIX-5251BA | NA | √ | X | X | X | X
| MIX-5251RBA | NA | √ | X | X | X | X
| MIX-5251HA | NA | √ | X | X | X | X
| MIX-502MA | NA | √ | X | X | X | X
| MIX-M500RA | NA | √ | X | X | X | X
| MIX-M500SA | NA | √ | X | X | X | X
| MIX-M500DMA | NA | √ | X | X | X | X
System Sensor
| 5551A | NA | √ | X | X | X | X
| 5551RA | NA | √ | X | X | X | X
| 5251PA | NA | √ | X | X | X | X
| 5251RPA | NA | √ | X | X | X | X
| M500X | NA | √ | X | X | X | X
| B524BIA | NA | √ | X | X | X | X
| B501B | NA | √ | X | X | X | X
| IM-10A | NA | √ | X | X | X | X
| CR-6A | NA | √ | X | X | X | X
| SC-6A | NA | √ | X | X | X | X
| FTX-P1A | NA | √ | X | X | X | X
| C2-6A | NA | √ | X | X | X | X
| 1251(B) | NA | √ | X | X | X | X
| 2251/T | NA | √ | X | X | X | X
| 2551TM-R | NA | √ | X | X | X | X
| 7251 | NA | √ | X | X | X | X
| M5251P/RP | NA | √ | X | X | X | X
| Smoke Detector Model Number | Base
Apollo
| 55000-225 | NA | √ | √ | √⁵ | √⁵ | √⁵
| 55000-325 | NA | √ | √ | √⁵ | √⁵ | √⁵
Hochiki
| DCD-135 | NS6-220 | √ | √ | √⁶ | √⁶ | √⁶
| DCD-135 | NS4-220 | √ | √ | √⁶ | √⁶ | √⁶
| DCD-135 | HSC-220R | √ | √ | √⁶ | √⁶ | √⁶
| DCD-190 | NS6-220 | √ | √ | √⁶ | √⁶ | √⁶
| DCD-190 | NS4-220 | √ | √ | √⁶ | √⁶ | √⁶
| DCD-190 | HSC-220R | √ | √ | √⁶ | √⁶ | √⁶
| SIJ-24 | NS6-220 | √ | √ | √⁶ | √⁶ | √⁶
| SIJ-24 | NS4-220 | √ | √ | √⁶ | √⁶ | √⁶
| SIJ-24 | HSC-220R | √ | √ | √⁶ | √⁶ | √⁶
| SLR-24 | NS6-220 | √ | √ | √⁶ | √⁶ | √⁶
| SLR-24 | NS4-220 | √ | √ | √⁶ | √⁶ | √⁶
| SLR-24 | HSC-220R | √ | √ | √⁶ | √⁶ | √⁶
| SLR-24H | NS6-220 | √ | √ | √⁶ | √⁶ | √⁶
| SLR-24H | NS4-220 | √ | √ | √⁶ | √⁶ | √⁶
| SLR-24H | HSC-220R | √ | √ | √⁶ | √⁶ | √⁶
| SLR-835 | NS6-220 | √ | √ | √⁶ | √⁶ | √⁶
| SLR-835 | NS4-220 | √ | √ | √⁶ | √⁶ | √⁶
| SLR-835 | HSC-220R | √ | √ | √⁶ | √⁶ | √⁶
| SLR-835B-2 | NA | √ | √ | √⁶ | √⁶ | √⁶
| SLR-835 | NS6-220 | X | X | √⁶ | √⁶ | √⁶
| 4451HT | B401 | X | X | √⁶ | √⁶ | √⁶
| 5451 | B401B | X | X | √⁶ | √⁶ | √⁶
| 5451 | B401 | X | X | √⁶ | √⁶ | √⁶
System Sensor
| 1400 | NA | √ | √ | √ | √ | √
| 2400 | NA | √ | √ | √ | √ | √
| 1151A | NA | √ | √ | √ | √ | √
| 2151A | NA | √ | √ | √ | √ | √
| C2W-BA | NA | √ | √ | √ | √ | √
| C2WT-BA | NA | √ | √ | √ | √ | √
| C2WTR-BA |  | X | √ | √ | √ | √
| 1451 | B401B | √ | √ | √ | √ | √
| 1451 | B406B | √ | √ | √ | √ | √
| 2451 | B401B | √ | √ | √ | √ | √
| 2451 | B406B | √ | √ | √ | √ | √
| 1451DH | DH400A | √ | √ | √ | √ | √
| 2451-A | DH400A | √ | √ | √ | √ | √
GE/Edwards
| 6249C | NA | √ | √ | √ | √ | √
| 6250C | NA | √ | √ | √ | √ | √
| 6264C | NA | √ | √ | √ | √ | √
| 6266C | NA | √ | √ | √ | √ | √
| 6269C | NA | √ | √ | √ | √ | √
| 6270C | NA | √ | √ | √ | √ | √
| 6269C-003 | NA | √ | √ | √ | √ | √
| 6270C-003 | NA | √ | √ | √ | √ | √
| C2M-PD1² | NA | √ | √ | √ | √ | √
Cerebrus Pyrotronics (Siemens)
| DI-2 | NA | √ | √ | X | X | X
| DI-3 | DB-3S | √ | √ | √ | √ | √
Sentrol-ESL (GE)
| 429C | NA | X | X | √ | √ | √
| 429CT | NA | X | X | √ | √ | √
| 429CST | NA | X | X | √ | √ | √
| 429CRT | NA | X | X | √ | √ | √
| 711U | 701E | X | X | √ | √ | √
| 711U | 701U | X | X | √ | √ | √
| 711U | 702E | X | X | √ | √ | √
| 711U | 702U | X | X | √ | √ | √
| 713-5U | 701E | X | X | √ | √ | √
| 713-5U | 701U | X | X | √ | √ | √
| 713-5U | 702E | X | X | √ | √ | √
| 713-5U | 702U | X | X | √ | √ | √
| 721U | 702E | X | X | √ | √ | √
| 721U | 702U | X | X | √ | √ | √
| 732U | 701E | X | X | √ | √ | √
| 732U | 701U | X | X | √ | √ | √
| 732U | 702E | X | X | √ | √ | √
| 732U | 702U | X | X | √ | √ | √
Detection Systems Inc.
| DS250 | NA | X | X | √ | √ | √
| DS250TH | NA | X | X | √ | √ | √
| DS282 | NA | X | X | √ | √ | √
| DS282TH | NA | X | X | √ | √ | √
Mircom
| MIR-525 | NA | √ | √ | √ | √ | √
| MIR-525T | NA | √ | √ | √ | √ | √
| MIR-1400A | NA | √ | √ | √ | √ | √
| MIR-2400A | NA | √ | √ | √ | √ | √
Mirtone
| 73471 | NA | √ | √ | X | X | X
| 73494 | NA | √ | √ | X | X | X
| 73575 | NA | √ | √ | X | X | X
| 73495 | 73486 | √ | √ | X | X | X
| 73495 | 73487 | √ | √ | X | X | X
| 73595 | 73486 | √ | √ | X | X | X
| 73595 | 73497 | √ | √ | X | X | X
| 73594 | 73400 | √ | √ | X | X | X
| 73405 | 73400 | √ | √ | X | X | X
| 73594 | 73401 | √ | √ | X | X | X
| 73405 | 73401 | √ | √ | X | X | X
Napco
| FW-2 | NA | √ | √ | √ | √ | √
Simplex/Grinnell (Tyco)
| 2098-9110 |  | √ | √ | X | X | X
Fenwal
| PSD-7131 | 70-201000-001 | √ | √ | X | X | X
| PSD-7131 | 70-201000-002 | √ | √ | X | X | X
| PSD-7131 | 70-201000-003 | √ | √ | X | X | X
| PSD-7131 | 70-201000-005 | √ | √ | X | X | X
| PSD-7130 | 70-201000-001 | √ | √ | X | X | X
| PSD-7130 | 70-201000-002 | √ | √ | X | X | X
| PSD-7130 | 70-201000-003 | √ | √ | X | X | X
| PSD-7130 | 70-201000-005 | √ | √ | X | X | X
| PSD-7126 | 70-201000-001 | √ | √ | X | X | X
| PSD-7126 | 70-201000-002 | √ | √ | X | X | X
| PSD-7126 | 70-201000-003 | √ | √ | X | X | X
| PSD-7126 | 70-201000-005 | √ | √ | X | X | X
| PSD-7129 | 70-201000-000 | √ | √ | X | X | X
| PSD-7125 | 70-201000-001 | √ | √ | X | X | X
| PSD-7125 | 70-201000-002 | √ | √ | X | X | X
| PSD-7125 | 70-201000-003 | √ | √ | X | X | X
| PSD-7125 | 70-201000-005 | √ | √ | X | X | X
| CPD-7021 | 70-201000-001 | √ | √ | X | X | X
| CPD-7021 | 70-201000-002 | √ | √ | X | X | X
| CPD-7021 | 70-201000-003 | √ | √ | X | X | X
| CPD-7021 | 70-201000-005 | √ | √ | X | X | X
Max stand-by current of all detectors not to exceed 3mA
Legend: | √ = Compatible
X = Not Compatible
Notes: | (1) Must use specified base
(2) CM2M-PD1 is a direct replacement for Edwards Models 6249C & 6251C and may be used on all panels where these detectors were cross-listed (CM2M-PDC has "Clean Me" technology and may NOT function with some panel models)
(3) Compatible only with "Clean Me" option "OFF"
(4) Do NOT mix model 1400 and 2400 smoke detectors on the same circuit with System Sensor 1151/1451 or System Sensor 2151/2451
(5) Compatibility identifier for head/base assembly: 5500-225/45681-251, -255, -256, -258
(6) Compatibility identifiers for head/base assemblies: A -A, HD-6, HD-3/HB-72, HB-3
Compatibility Issues: | Maximum stand-by current of all detectors in an initiating circuit cannot exceed 3.0 milli-Amps.
Copyright © 2008 by Frank Kurz (All Rights Reserved)

## Notifier
| Compatible Analog Loop Devices | Notifier Panel Models | AFP-200 | AFP-300/400 | AFC-600/NFS-640 | NFS2-640 | NFS-320 | NFS-3030 | AM2020/AFP-1010 | RP-1001 | RP-1002 | S500(TC-2/TC-4) | S5000 (TCM-2/TCM-4) | XP5-C | FCM-1
System Sensor
| 2W-BA | NA | √ | X | X | X | X
| 5551RA | NA | √ | X | X | X | X
| 5251PA | NA | √ | X | X | X | X
| 5251RPA | NA | √ | X | X | X | X
| M500X | NA | √ | X | X | X | X
| B524BIA | NA | √ | X | X | X | X
| B501B | NA | √ | X | X | X | X
| IM-10A | NA | √ | X | X | X | X
| CR-6A | NA | √ | X | X | X | X
| SC-6A | NA | √ | X | X | X | X
| FTX-P1A | NA | √ | X | X | X | X
| C2-6A | NA | √ | X | X | X | X
| 1251(B) | NA | √ | X | X | X | X
| 2251/T | NA | √ | X | X | X | X
| 2551TM-R | NA | √ | X | X | X | X
| 7251 | NA | √ | X | X | X | X
| M5251P/RP | NA | √ | X | X | X | X
| Smoke Detector Model Number | Base
Apollo
| 55000-225 | NA | √ | √ | √⁵ | √⁵ | √⁵
| 55000-325 | NA | √ | √ | √⁵ | √⁵ | √⁵
Hochiki
| DCD-135 | NS6-220 | √ | √ | √⁶ | √⁶ | √⁶
| DCD-135 | NS4-220 | √ | √ | √⁶ | √⁶ | √⁶
| DCD-135 | HSC-220R | √ | √ | √⁶ | √⁶ | √⁶
| DCD-190 | NS6-220 | √ | √ | √⁶ | √⁶ | √⁶
| DCD-190 | NS4-220 | √ | √ | √⁶ | √⁶ | √⁶
| DCD-190 | HSC-220R | √ | √ | √⁶ | √⁶ | √⁶
| SIJ-24 | NS6-220 | √ | √ | √⁶ | √⁶ | √⁶
| SIJ-24 | NS4-220 | √ | √ | √⁶ | √⁶ | √⁶
| SIJ-24 | HSC-220R | √ | √ | √⁶ | √⁶ | √⁶
| SLR-24 | NS6-220 | √ | √ | √⁶ | √⁶ | √⁶
| SLR-24 | NS4-220 | √ | √ | √⁶ | √⁶ | √⁶
| SLR-24 | HSC-220R | √ | √ | √⁶ | √⁶ | √⁶
| SLR-24H | NS6-220 | √ | √ | √⁶ | √⁶ | √⁶
| SLR-24H | NS4-220 | √ | √ | √⁶ | √⁶ | √⁶
| SLR-24H | HSC-220R | √ | √ | √⁶ | √⁶ | √⁶
| SLR-835 | NS6-220 | √ | √ | √⁶ | √⁶ | √⁶
| SLR-835 | NS4-220 | √ | √ | √⁶ | √⁶ | √⁶
| SLR-835 | HSC-220R | √ | √ | √⁶ | √⁶ | √⁶
| SLR-835B-2 | NA | √ | √ | √⁶ | √⁶ | √⁶
| SLR-835 | NS6-220 | X | X | √⁶ | √⁶ | √⁶
| 4451HT | B401 | X | X | √⁶ | √⁶ | √⁶
| 5451 | B401B | X | X | √⁶ | √⁶ | √⁶
| 5451 | B401 | X | X | √⁶ | √⁶ | √⁶
System Sensor
| 1400 | NA | √ | √ | √ | √ | √
| 2400 | NA | √ | √ | √ | √ | √
| 1151A | NA | √ | √ | √ | √ | √
| 2151A | NA | √ | √ | √ | √ | √
| C2W-BA | NA | √ | √ | √ | √ | √
| C2WT-BA | NA | √ | √ | √ | √ | √
| C2WTR-BA |  | X | √ | √ | √ | √
| 1451 | B401B | √ | √ | √ | √ | √
| 1451 | B406B | √ | √ | √ | √ | √
| 2451 | B401B | √ | √ | √ | √ | √
| 2451 | B406B | √ | √ | √ | √ | √
| 1451DH | DH400A | √ | √ | √ | √ | √
| 2451-A | DH400A | √ | √ | √ | √ | √
GE/Edwards
| 6249C | NA | X | X | X | X | X
| 6250C | NA | √ | √ | √ | √ | √
| 6264C | NA | √ | √ | √ | √ | √
| 6266C | NA | √ | √ | √ | √ | √
| 6269C | NA | √ | √ | √ | √ | √
| 6270C | NA | √ | √ | √ | √ | √
| 6269C-003 | NA | √ | √ | √ | √ | √
| 6270C-003 | NA | √ | √ | √ | √ | √
| C2M-PD1 | NA | √ | √ | √ | √ | √
Cerebrus Pyrotronics (Siemens)
| DI-2 | NA | √ | √ | X | X | X
| DI-3 | DB-3S | √ | √ | √ | √ | √
Sentrol-ESL (GE)
| 429C | NA | X | X | √ | √ | √
| 429CT | NA | X | X | √ | √ | √
| 429CST | NA | X | X | √ | √ | √
| 429CRT | NA | X | X | √ | √ | √
| 711U | 701E | X | X | √ | √ | √
| 711U | 701U | X | X | √ | √ | √
| 711U | 702E | X | X | √ | √ | √
| 711U | 702U | X | X | √ | √ | √
| 713-5U | 701E | X | X | √ | √ | √
| 713-5U | 701U | X | X | √ | √ | √
| 713-5U | 702E | X | X | √ | √ | √
| 713-5U | 702U | X | X | √ | √ | √
| 721U | 702E | X | X | √ | √ | √
| 721U | 702U | X | X | √ | √ | √
| 732U | 701E | X | X | √ | √ | √
| 732U | 701U | X | X | √ | √ | √
| 732U | 702E | X | X | √ | √ | √
| 732U | 702U | X | X | √ | √ | √
Detection Systems Inc.
| DS250 | NA | X | X | √ | √ | √
| DS250TH | NA | X | X | √ | √ | √
| DS282 | NA | X | X | √ | √ | √
| DS282TH | NA | X | X | √ | √ | √
Mircom
| MIR-525 | NA | √ | √ | √ | √ | √
| MIR-525T | NA | √ | √ | √ | √ | √
| MIR-1400A | NA | √ | √ | √ | √ | √
| MIR-2400A | NA | √ | √ | √ | √ | √
Mirtone
| 73471 | NA | √ | √ | X | X | X
| 73494 | NA | √ | √ | X | X | X
| 73575 | NA | √ | √ | X | X | X
| 73495 | 73486 | √ | √ | X | X | X
| 73495 | 73487 | √ | √ | X | X | X
| 73595 | 73486 | √ | √ | X | X | X
| 73595 | 73497 | √ | √ | X | X | X
| 73594 | 73400 | √ | √ | X | X | X
| 73405 | 73400 | √ | √ | X | X | X
| 73594 | 73401 | √ | √ | X | X | X
| 73405 | 73401 | √ | √ | X | X | X
Napco
| FW-2 | NA | √ | √ | √ | √ | √
Simplex/Grinnell (Tyco)
| 2098-9110 |  | √ | √ | X | X | X
Fenwal
| PSD-7131 | 70-201000-001 | √ | √ | X | X | X
| PSD-7131 | 70-201000-002 | √ | √ | X | X | X
| PSD-7131 | 70-201000-003 | √ | √ | X | X | X
| PSD-7131 | 70-201000-005 | √ | √ | X | X | X
| PSD-7130 | 70-201000-001 | √ | √ | X | X | X
| PSD-7130 | 70-201000-002 | √ | √ | X | X | X
| PSD-7130 | 70-201000-003 | √ | √ | X | X | X
| PSD-7130 | 70-201000-005 | √ | √ | X | X | X
| PSD-7126 | 70-201000-001 | √ | √ | X | X | X
| PSD-7126 | 70-201000-002 | √ | √ | X | X | X
| PSD-7126 | 70-201000-003 | √ | √ | X | X | X
| PSD-7126 | 70-201000-005 | √ | √ | X | X | X
| PSD-7129 | 70-201000-000 | √ | √ | X | X | X
| PSD-7125 | 70-201000-001 | √ | √ | X | X | X
| PSD-7125 | 70-201000-002 | √ | √ | X | X | X
| PSD-7125 | 70-201000-003 | √ | √ | X | X | X
| PSD-7125 | 70-201000-005 | √ | √ | X | X | X
| CPD-7021 | 70-201000-001 | √ | √ | X | X | X
| CPD-7021 | 70-201000-002 | √ | √ | X | X | X
| CPD-7021 | 70-201000-003 | √ | √ | X | X | X
| CPD-7021 | 70-201000-005 | √ | √ | X | X | X
Max stand-by current of all detectors not to exceed 3mA
Legend: | √ = Compatible
X = Not Compatible
Notes: | (1) Must use specified base
(2) CM2M-PD1 is a direct replacement for Edwards Models 6249C & 6251C and may be used on all panels where these detectors were cross-listed (CM2M-PDC has "Clean Me" technology and may NOT function with some panel models)
(3) Compatible only with "Clean Me" option "OFF"
(4) Do NOT mix model 1400 and 2400 smoke detectors on the same circuit with System Sensor 1151/1451 or System Sensor 2151/2451
(5) Compatibility identifier for head/base assembly: 5500-225/45681-251, -255, -256, -258
(6) Compatibility identifiers for head/base assemblies: A -A, HD-6, HD-3/HB-72, HB-3
Compatibility Issues: | Maximum stand-by current of all detectors in an initiating circuit cannot exceed 3.0 milli-Amps.
Copyright © 2008 by Frank Kurz (All Rights Reserved)